{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["765송부","345송부","154송부"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":12,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"765송부","index":0,"n_rows":10,"n_cols":11,"rows_kept":10,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 9월 휴전계획서"]
["765kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"경기","성남","신안성S/S #4 M.Tr A-1","20년 성남전력 변전정비 총액공사","변압기보호반대체","2020-09-21 09:00","2020-10-23 18:00","취소","취소","연속"]
[2,"경기","성남","신안성신가평 T/L","2020-2021년 성남전력지사 가공송전정비회사 총액공사","- 765kV 신안성-신가평T/L 항공장애표시도장(22기)","2020-09-01 07:00","2020-09-29 18:00","2020-09-01 07:00","2020-09-29 18:00","연속"]
[3,"강원","태백","신태백S/S 765kV #2 BUS","2020년 신태백S/S 800kV GIS 보통점검","DS(8352, 8452, 8652), ES+VT(#2BUS) 보통점검","2020-09-10 09:00","2020-09-11 18:00","취소","취소","연속"]
[4,"강원","태백","신태백S/S 765kV #1 BUS","2020년 신태백S/S 800kV GIS 보통점검","DS(8351, 8451, 8651), ES+VT(#1BUS) 보통점검","2020-09-08 09:00","2020-09-09 18:00","취소","취소","연속"]
[5,"충북","직할","신중부S/S 765kV CB 8571","신중부S/S 765kV #3M.Tr 1차 GIS 설치공사","o 765kV GIS 1CB 설치 o 기타 부대공사 1식","2020-09-02 09:00","2020-09-04 18:00","2020-09-02 09:00","2020-09-04 18:00","연속"]
[6,"경북","영주","신한울S/S #2 M.Tr A-1","2020-21년 영주전력지사 변전정비회사 총액공사","- YPP 계전기 성능개선 - #2M.Tr B-2상 권선온도계 교체 - B-2상 중압 부싱 접지선 과열 및 고압권선 온도 상한 경보 조치 - B-2상 탭가드 히터 불량 조치 - A-1상 탭가드 온도센서 불량 조치 - M.Tr 원격제어반 C-1상 TPI 교체 - C-1상 4그룹 B상 모터 불량 조치","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]

{"sheet":"345송부","index":1,"n_rows":239,"n_cols":11,"rows_kept":239,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 9월 휴전계획서"]
["345kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","성동","성동S/S #1 M.Tr","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020-09-14 09:30","2020-09-25 18:00","2020-09-14 09:30","2020-09-25 18:00","연속"]
[2,"서울","중부","중부S/S 345kV #70 BUS","중부S/S 345kV 7351DS 이음발생 점검공사","중부S/S 345kV 7351DS 이음발생 점검공사","2020-09-08 10:00","2020-09-10 18:00","2020-09-08 10:00","2020-09-10 18:00","연속"]
[3,"서울","중부","중부S/S #1 M.Tr","`20 중부P/O 변전정비회사 총액공사","M.Tr 초기점검","2020-09-02 10:00","2020-09-04 18:00","2020-09-02 10:00","2020-09-04 18:00","연속"]
[4,"남서울","영등포","서서울신광명#1 T/L","신광명S/S 345kV 송전선로 보호반 교체공사","- 서서울-신광명#1T/L 노후 송전선로 보호반 교체 시행","2020-09-21 09:00","2020-09-25 18:00","2020-09-21 09:00","2020-09-25 18:00","연속"]
[5,"남서울","직할","영등포S/S #1 M.Tr","영등포S/S 345kV 주변압기 정밀점검","영등포S/S 345kV 주변압기 정밀점검 상판누유보수, 3차 PT 교체","2020-09-09 09:00","2020-09-25 18:00","2020-09-09 09:00","2020-09-25 18:00","연속"]
[6,"인천","김포","가정개폐소 345kV CB 7372","가정개폐소 345kV 가정-갈산#2T/L GIS 초기점검","가정개폐소 345kV 가정-갈산#2T/L GIS(7372 CB) 초기점검","2020-09-24 10:00","2020-09-24 18:00","2020-09-24 10:00","2020-09-24 18:00","연속"]
[7,"인천","김포","가정개폐소 345kV CB 7300","가정개폐소 345kV 신가좌-가정#2T/L TIE GIS 보통점검","가정개폐소 345kV 신가좌-가정#2T/L TIE GIS(7300 CB) 보통점검","2020-09-23 10:00","2020-09-23 18:00","2020-09-23 10:00","2020-09-23 18:00","연속"]
[8,"인천","김포","가정개폐소 345kV CB 7371","가정개폐소 345kV 신가좌-가정#2T/L GIS 보통점검","가정개폐소 345kV 신가좌-가정#2T/L GIS(7371 CB) 보통점검","2020-09-22 10:00","2020-09-22 18:00","2020-09-22 10:00","2020-09-22 18:00","연속"]
[9,"인천","김포","가정개폐소 345kV CB 7471","가정개폐소 345kV 가정-인천CC#1T/L GIS 보통점검","가정개폐소 345kV 가정-인천CC#1T/L GIS(7471 CB) 보통점검","2020-09-21 10:00","2020-09-21 18:00","2020-09-21 10:00","2020-09-21 18:00","연속"]
[10,"인천","김포","신김포신인천CC T/L","345kV 신김포-신인천CC T/L 잔여 접속함 해체점검","공사대상 : (1B) J/B#1,3,4-1,7 / (2B) J/B#1,2,4-1,7 공사내용 : 접속함 해체점검","2020-09-22 08:00","2020-09-24 20:00","2020-09-22 08:00","2020-09-24 20:00","연속"]
[11,"인천","부평","신가좌신시흥#1 T/L","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -73Bay 철거 및 설치 -제어케이블 분리 및 결선","2020-09-25 09:00","2020-12-04 18:00","2020-09-25 09:00","2020-12-04 18:00","연속"]
[12,"인천","부평","신가좌S/S #2 M.Tr","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -73Bay 철거 및 설치 -제어케이블 분리 및 결선","2020-09-25 09:00","2020-12-04 18:00","2020-09-25 09:00","2020-12-04 18:00","연속"]
[13,"인천","부평","신인천C/C 345kV CB 7572","서인천복합S/Y 362kV 7572 GIS 보통점검 공사","서인천복합S/Y 362kV 7572 GIS 보통점검 공사","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[14,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥S/S 345kV #1M.Tr 2차 GIS정밀점검","신시흥S/S 345kV #1M.Tr 2차 GIS정밀점검","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[15,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥S/S 154kV 6100TIE GIS정밀 무부하(#1M.Tr휴전)","신시흥S/S 154kV 6100TIE GIS정밀 무부하(#1M.Tr휴전)","2020-09-19 16:00","2020-09-19 18:00","2020-09-19 16:00","2020-09-19 18:00","연속"]
[16,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥S/S 65-66SEC GIS정밀 무부하(#1M.Tr휴전)","신시흥S/S 154kV 65-66SEC GIS정밀 무부하(#1M.Tr휴전)","2020-09-17 16:00","2020-09-17 18:00","2020-09-17 16:00","2020-09-17 18:00","연속"]
[17,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥S/S 60-61SEC GIS정밀 무부하(#1M.Tr휴전)","신시흥S/S 154kV 60-61SEC GIS정밀 무부하(#1M.Tr휴전)","2020-09-15 16:00","2020-09-15 18:00","2020-09-15 16:00","2020-09-15 18:00","연속"]
[18,"인천","시흥","신시흥#2S/S #6 M.Tr","신시흥S/S 345kV #6M.Tr 2차 GIS정밀점검","신시흥S/S 345kV #6M.Tr 2차 GIS정밀점검","2020-09-28 09:00","2020-09-29 18:00","2020-09-28 09:00","2020-09-29 18:00","연속"]
[19,"인천","시흥","신시흥#2S/S #5 M.Tr","신시흥S/S 345kV #5M.Tr 2차 GIS정밀점검","신시흥S/S 345kV #5M.Tr 2차 GIS정밀점검","2020-09-23 09:00","2020-09-24 18:00","2020-09-23 09:00","2020-09-24 18:00","연속"]
[20,"경기북부","고양","신덕은S/S #3 M.Tr","345kV 신덕은S/S 종합 예방진단시스템 설치공사","○ DGA 설치 ○ OLTC UHF 센서 설치 ○ OLTC 진단장치 설치","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[21,"경기북부","고양","신덕은동두천CC#2 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 정밀점검","2020-09-29 08:00","2020-09-29 18:00","2020-09-29 08:00","2020-09-29 18:00","매일"]
[22,"경기북부","고양","신덕은S/S #2 M.Tr","345kV 신덕은S/S 종합 예방진단시스템 설치공사","○ DGA 설치 ○ OLTC UHF 센서 설치 ○ OLTC 진단장치 설치","2020-09-08 09:00","2020-09-11 18:00","2020-09-08 09:00","2020-09-11 18:00","연속"]
[23,"경기북부","고양","신파주신덕은#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 정밀점검","2020-09-03 08:00","2020-09-05 18:00","2020-09-03 08:00","2020-09-05 18:00","연속"]
[24,"경기북부","고양","신파주S/S #3 M.Tr","20년 고양P/O 변전정비회사 총액공사","신파주S/S #3M.Tr 누유보수(B상 96P, C상 상판 등)","2020-09-21 10:00","2020-09-21 18:00","2020-09-21 10:00","2020-09-21 18:00","연속"]
[25,"경기북부","고양","신김포신파주#1 T/L","362kV GIS 보통점검 - 변전총액공사","신파주S/S 7100, 7172 GIS 보통점검","2020-09-17T10:00:00","2020-09-18T18:00:00","2020-09-17T10:00:00","2020-09-18T18:00:00","연속"]
[26,"경기북부","고양","신파주신덕은#2 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-08 07:00","2020-09-11 18:00","2020-09-08 07:00","2020-09-11 18:00","연속"]
[27,"경기북부","고양","신파주양주#1 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 철탑 2기 신설(신설 1기) ㅇ 철탑 2기 철거(임시 1기, 기설 1기) ㅇ 전선 공중이동 및 전선당기기(현수→내장) ㅇ 뒷정리 및 준공(2020. 9월)","2020-09-15 07:00","2020-09-17 18:00","취소","취소","연속"]
[28,"경기북부","고양","신파주양주#1 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 철탑 2기 신설(신설 1기) ㅇ 철탑 2기 철거(임시 1기, 기설 1기) ㅇ 전선 공중이동 및 전선당기기(현수→내장) ㅇ 뒷정리 및 준공(2020. 9월)","2020-09-23 07:00","2020-09-27 18:00","취소","취소","연속"]
[29,"경기북부","고양","신파주양주#2 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 철탑 2기 신설(신설 1기) ㅇ 철탑 2기 철거(임시 1기, 기설 1기) ㅇ 전선 공중이동 및 전선당기기(현수→내장) ㅇ 뒷정리 및 준공(2020. 9월)","2020-09-18 07:00","2020-09-22 18:00","취소","취소","연속"]
[30,"경기북부","구리","신의정부미금#1 T/L","20~21년 경기북부 직할 가공송전정비회사 총액공사","압축인류크램프 및 점퍼선교체","2020-09-25 08:00","2020-09-25 14:00","2020-09-25 08:00","2020-09-25 14:00","연속"]
[31,"경기북부","구리","신가평미금#1 T/L","'20-21년 구리전력지사 변전정비회사 총액공사","장기사용 배전반 교체공사 - 345kV 신가평-미금#1T/L 보호반 교체","2020-09-14 09:00","2020-09-23 18:00","취소","취소","연속"]
[32,"경기북부","구리","신가평신의정부#2 T/L","20~21년 경기북부 직할 가공송전정비회사 총액공사","ㅇ 점퍼선교체 ㅇ 항공장애표시구 설치","2020-09-25 14:00","2020-09-25 12:00","2020-09-25 14:00","2020-09-25 18:00","연속"]
[33,"경기북부","구리","신가평신의정부#1 T/L","345kV 신가평-신의정부#1T/L 정밀점검","- No.45~48, 96,97 정밀점검","2020-09-24 08:30","2020-09-24 18:00","2020-09-24 08:30","2020-09-24 18:00","연속"]
[34,"경기북부","구리","신포천S/S #1 M.TR","2020년도 구리전력지사 345kV 주변압기 점검 공사","신포천S/S 345kV #1M.Tr 정밀점검 공사","2020-09-14 10:00","2020-09-29 18:00","2020-09-16 09:00","2020-09-16 18:00","연속"]
[35,"경기북부","구리","신포천포천LNGCC#1 T/L","구리전력지사 345kV GIS 보통점검","구리전력지사 345kV GIS 보통점검","2020-09-14 09:00","2020-09-15 18:00","2020-09-14 09:00","2020-09-15 18:00","매일"]
[36,"경기북부","구리","신포천포천LNGCC#2 T/L","구리전력지사 345kV GIS 보통점검","구리전력지사 345kV GIS 보통점검","2020-09-17 09:00","2020-09-17 18:00","2020-09-17 09:00","2020-09-17 18:00","연속"]
[37,"경기북부","직할","신포천동두천CC#2 T/L","2020년 가공송전선로 순시점검 위탁공사","정밀점검","2020-09-14 08:00","2020-09-16 18:00","취소","취소","연속"]
[38,"경기북부","직할","신덕은동두천CC#1 T/L","2020년 가공송전선로 순시점검 위탁공사","정밀점검","2020-09-14 08:00","2020-09-21 18:00","취소","취소","연속"]
[39,"경기북부","직할","양주S/S #4 M.Tr","양주변전소 옥외철구 GIS화 공사","배전반 이설 및 제어케이블 설치","2020-09-10 09:00","2020-09-21 18:00","2020-09-10 09:00","2020-09-21 18:00","매일"]
[40,"경기북부","직할","신의정부양주#1 T/L","양주변전소 옥외철구 GIS화 공사","배전반 이설 및 제어케이블 설치","2020-09-14 09:00","2020-09-21 18:00","2020-09-14 09:00","2020-09-21 18:00","매일"]
[41,"경기북부","직할","양주S/S #4 M.Tr","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[42,"경기북부","직할","양주S/S #2 M.Tr","양주변전소 옥외철구 GIS화관련 전력케이블 설치공사","M.Tr 2차 전력케이블 EBA 설치","2020-09-08 09:00","2020-09-09 18:00","2020-09-08 09:00","2020-09-09 18:00","매일"]
[43,"경기북부","직할","양주S/S #1 M.Tr","양주변전소 옥외철구 GIS화관련 전력케이블 설치공사","M.Tr 2차 전력케이블 EBA 설치","2020-09-03 09:00","2020-09-04 18:00","2020-09-03 09:00","2020-09-04 18:00","매일"]
[44,"경기","군포","신시흥신안산#2 T/L","신안산S/S 신시흥-신안산#2T/L 보호반 성능개선(영인)","신안산S/S 신시흥-신안산#2T/L 보호반 성능개선(영인)","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[45,"경기","동부","곤지암S/S 345kV #1 Sh.R","20년 동부 변전정비회사 총액공사","곤지암:#1Sh.R GIS(조작), 7179(A,B,C)GIS전자변교체,전자변실리콘히터 설치(A,B,C) 43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-09-24 09:30","2020-09-24 18:00","2020-09-24 09:30","2020-09-24 18:00","연속"]
[46,"경기","성남","신성남S/S #6 M.Tr","20년 성남전력지사 변전정비회사 총액공사","96D회로보완, 7872CB 보통점검 및 전자변 교체 등","2020-09-18 09:00","2020-09-18 18:00","2020-09-18 09:00","2020-09-18 18:00","연속"]
[47,"경기","성남","신성남S/S #4 M.Tr","20년 성남전력지사 변전정비회사 총액공사","96D회로보완, 7572CB 전자변 교체 등","2020-09-17 09:00","2020-09-17 18:00","2020-09-17 09:00","2020-09-17 18:00","연속"]
[48,"경기","성남","신성남S/S #1 M.Tr","20년 성남전력지사 변전정비회사 총액공사","96D회로보완, 7172CB 보통점검 및 전자변교체 등","2020-09-14 09:00","2020-09-15 18:00","2020-09-14 09:00","2020-09-15 18:00","연속"]
[49,"경기","성남","신성남S/S #3 M.Tr","20년 성남전력지사 변전정비회사 총액공사","96D회로보완, LCP 보조계전기 교체 등","2020-09-16 09:00","2020-09-16 18:00","2020-09-16 09:00","2020-09-16 18:00","연속"]
[50,"경기","성남","신성남S/S #2 M.Tr","20년 성남전력 변전정비회사 총액공사","- #2M.Tr GIS(조작),전자변교체 - 3차측 MAIN GIS(보통) - 1S.Tr GIS(보통) - STATCOM 2S.Tr GIS(보통) - 부싱절연유채유","2020-09-17 09:00","2020-09-18 18:00","2020-09-17 09:00","2020-09-18 18:00","연속"]
[51,"경기","성남","서서울#2신성남#1 T/L","서서울2-신성남 스페이서 간격조정","서서울2-신성남 스페이서 간격조정 - 1806개, 38경간","2020-09-19 08:00","2020-09-24 18:00","2020-09-19 08:00","2020-09-24 18:00","연속"]
[52,"경기","성남","서서울#2신성남#2 T/L","서서울2-신성남 스페이서 간격조정","서서울2-신성남 스페이서 간격조정 - 1806개, 38경간","2020-09-25 08:00","2020-09-29 18:00","2020-09-25 08:00","2020-09-29 18:00","연속"]
[53,"경기","성남","신안성신수원#2 T/L","신수원S/S 345kV 용량대체공사","GIS 대체 * 3CB","2020-09-01 09:00","2020-10-23 18:00","2020-09-01 09:00","2020-10-23 18:00","연속"]
[54,"경기","성남","신수원S/S 345kV #1 BUS","신수원S/S 345kV 용량대체공사","GIS 대체 * 3CB","2020-09-05 09:00","2020-09-23 18:00","2020-09-05 09:00","2020-09-23 18:00","연속"]
[55,"경기","성남","신수원삼성#1 T/L","신수원S/S 345kV 용량대체공사","GIS 대체 * 3CB","2020-09-04 09:00","2020-11-24 18:00","2020-09-04 09:00","2020-11-24 18:00","연속"]
[56,"경기","성남","신안성S/S 345kV #5 Sh.R","2020년 성남전력 변전정비 총액공사","49T 회로보완(경보운전)","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[57,"경기","성남","신용인S/S #3 M.Tr","20년 성남전력 변전정비회사 총액공사","- 변압기보통점검 - 2차측 GIS(조작) - 전자변교체 - LA 1차(초기) - LA 2차(대체) - LA 3차(초기) - PT 3차(보통) - 96P 커버설치","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[58,"경기","성남","신용인S/S #1 M.Tr","2020년 성남전력 변전정비 총액공사","96D 회로보완(경보운전)","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[59,"경기","직할","아산화성#1 T/L","영인 보호계전기 성능개선 작업","화성S/S 아산화성#1 T/L 영인 보호계전기 성능개선 작업","2020-09-08 09:00","2020-09-08 14:00","취소","취소","연속"]
[60,"경기","직할","화성신안산#1 T/L","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79Bay 환원작업","2020-09-07 08:00","2020-09-22 18:00","취소","취소","연속"]
[61,"경기","직할","아산화성#2 T/L","영인 보호계전기 성능개선 작업","화성S/S 아산화성#2 T/L 영인 보호계전기 성능개선 작업","2020-09-08 14:00","2020-09-08 18:00","취소","취소","연속"]
[62,"경기","직할","화성S/S 345kV #71 BUS","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79 Bay 임시이설 - #71BUS 무부하 가압 시행","2020-09-17 11:00","2020-09-18 11:00","취소","취소","연속"]
[63,"경기","직할","화성S/S 345kV #76 BUS","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79 Bay 임시이설 - #76BUS 무부하 가압 시행","2020-09-18 11:00","2020-09-19 11:00","취소","취소","연속"]
[64,"경기","직할","화성신평택CC#1 T/L","20년 직할 변전정비회사 총액공사","화성S/S 화성-신평택CC #1T/L, TIE GIS 하자(~18)","2020-09-23 09:00","2020-09-24 18:00","2020-09-23 09:00","2020-09-24 18:00","연속"]
[65,"경기","직할","화성신안산#2 T/L","345kV 화성S/S GIS 용량대체공사","- 화성신안산#2T/L 7A -> 7B Bay 임시이설","2020-09-23 08:00","2020-10-13 18:00","취소","취소","연속"]
[66,"경기","직할","화성신평택CC#2 T/L","20년 직할 변전정비회사 총액공사","화성S/S 화성-신평택CC #2T/L, TIE GIS, 상부 GIS 하자(~10)","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[67,"경기","평택","서안성S/S 345kV #2 BUS","345kV 서안성S/S 용량부족 GIS 대체공사","- 345kV GIS 50kA X 11CB 철거 - 345kV GIS 63kA X 11CB 철거","2020-09-29 09:00","2020-10-29 09:00","2020-09-29 09:00","2020-10-29 09:00","연속"]
[68,"경기","평택","서안성신진천#1 T/L","345kV 서안성S/S 용량부족 GIS 대체공사","- 345kV GIS 50kA X 11CB 철거 - 345kV GIS 63kA X 11CB 철거","2020-09-28 09:00","2020-09-29 09:00","취소","취소","연속"]
[69,"경기","평택","서안성S/S #2 M.Tr","345kV 서안성S/S 용량부족 GIS 대체공사","- 345kV GIS 50kA X 11CB 철거 - 345kV GIS 63kA X 11CB 철거","2020-09-01 09:00","2020-10-30 09:00","2020-09-01 09:00","2020-10-30 09:00","연속"]
[70,"경기","평택","서안성S/S 345kV #1 BUS","345kV 서안성S/S 용량부족 GIS 대체공사","- 345kV GIS 50kA X 11CB 철거 - 345kV GIS 63kA X 11CB 철거","2020-09-01 09:00","2020-09-29 09:00","2020-09-01 09:00","2020-09-29 09:00","연속"]
[71,"경기","평택","신안성서안성#1 T/L","345kV 서안성S/S 용량부족 GIS 대체공사","- 345kV GIS 50kA X 11CB 철거 - 345kV GIS 63kA X 11CB 철거","2020-09-01 09:00","2020-10-30 09:00","2020-09-01 09:00","2020-10-30 09:00","연속"]
[72,"강원","강릉","양양P/P 345kV CB 7200","2020년 345kV GIS 보통점검","○ 2020년 345kV GIS 보통점검","2020-09-16 10:00","2020-09-17 18:00","2020-09-16 10:00","2020-09-17 18:00","연속"]
[73,"강원","강릉","양양P/P 345kV CB 7172","2020년 345kV GIS 보통점검","○ 2020년 345kV GIS 보통점검","2020-09-15 10:00","2020-09-15 18:00","2020-09-15 10:00","2020-09-15 18:00","연속"]
[74,"강원","강릉","양양P/P 345kV CB 7271","2020년 345kV GIS 보통점검","○ 2020년 345kV GIS 보통점검","2020-09-16 10:00","2020-09-17 18:00","2020-09-16 10:00","2020-09-17 18:00","연속"]
[75,"강원","강릉","양양P/P 345kV CB 7272","2020년 345kV GIS 보통점검","○ 2020년 345kV GIS 보통점검","2020-09-18 10:00","2020-09-18 18:00","2020-09-18 10:00","2020-09-18 18:00","연속"]
[76,"강원","동해","동해S/S 345kV CB 7272","2020년 동해관내 362kV GIS 정밀점검","동해S/S 362kV 동해-북평TP#1 GIS 차단부(7272) 정밀점검","2020-09-22 09:00","2020-09-25 18:00","2020-09-22 09:00","2020-09-25 18:00","연속"]
[77,"강원","동해","동해삼척GP#1 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체 및 가공지선 불량개소정비","2020-09-09 08:00","2020-09-09 18:00","2020-09-09 08:00","2020-09-09 18:00","연속"]
[78,"강원","동해","동해삼척GP#2 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-10 08:00","2020-09-10 18:00","2020-09-10 08:00","2020-09-10 18:00","연속"]
[79,"강원","동해","동해S/S #1 M.Tr","#1M.Tr 제작사 하자처리 시행","1. #1M.Tr A 송유펌프 플렌지 누유개소 보수 시행","2020-09-22 09:00","2020-09-24 18:00","2020-09-22 09:00","2020-09-24 18:00","연속"]
[80,"강원","동해","삼척GP한울NP#1 T/L","2020년 가공송전선로 순시점검 위탁공사","송전선로 정밀점검","2020-09-14 08:00","2020-09-18 18:00","2020-09-14 08:00","2020-09-18 18:00","매일"]
[81,"강원","동해","삼척GP한울NP#2 T/L","2020년 가공송전선로 순시점검 위탁공사","송전선로 정밀점검","2020-09-21 08:00","2020-09-25 18:00","2020-09-21 08:00","2020-09-25 18:00","매일"]
[82,"강원","동해","삼척G/P 345kV CB 7772","2020년 동해P/O 변전정비회사 총액공사","삼척GP 345kV #1 Step-up TR GIS CB (7772) 보통점검","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[83,"충북","직할","신중부S/S 765kV CB 7B71","신중부S/S 345kV GIS 하자보수 공사","345kV DS(7B61) Limit 접점불량 보수","2020-09-09 09:00","2020-09-09 18:00","2020-09-09 09:00","2020-09-09 18:00","연속"]
[84,"충북","직할","신중부S/S 345kV #5 Sh.R","신중부S/S 345kV GIS 하자보수 공사","345kV GIS #5Sh.R 측 DS(7A21) 매커니즘 보수","2020-09-02 09:00","2020-09-04 18:00","2020-09-02 09:00","2020-09-04 18:00","연속"]
[85,"충북","직할","신중부S/S 345kV #6 Sh.R","765kV 신중부S/S 초기점검공사","765kV 신중부S/S 초기점검공사(#6Sh.R, 7C79, 7C71, 7C00)","2020-09-09 09:00","2020-09-11 18:00","2020-09-09 09:00","2020-09-11 18:00","연속"]
[86,"충북","직할","신중부S/S 765kV CB 7971","765kV 신중부S/S 초기점검공사","765kV 신중부S/S 초기점검공사(7971CB)","2020-09-16 09:00","2020-09-16 18:00","2020-09-16 09:00","2020-09-16 18:00","연속"]
[87,"충북","직할","신중부S/S 345kV CB 7A72","765kV 신중부S/S 초기점검공사","765kV 신중부S/S 초기점검공사(7A72)","2020-09-17 09:00","2020-09-17 18:00","2020-09-17 09:00","2020-09-17 18:00","연속"]
[88,"충북","직할","신중부S/S 345kV CB 7C72","765kV 신중부S/S 초기점검공사","765kV 신중부S/S 초기점검공사(7C72 CB)","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[89,"충북","직할","신진천S/S 345kV #1 BUS","345kV 신진천S/S 용량부족 GIS 대체공사 (#70BUS)","345kV GIS #70BUS 및 (#71~74BAY)51DS 대체(8차분)","2020-09-20 09:00","2020-10-20 18:00","2020-09-20 09:00","2020-10-20 18:00","연속"]
[90,"충북","직할","서안성신진천#2 T/L","345kV 신진천S/S 용량부족 GIS 대체공사 (#73BAY)","345kV GIS 40kA → 63kA 2CB 대체(7차분)","2020-09-04 09:00","2020-12-18 18:00","2020-09-04 09:00","2020-12-18 18:00","연속"]
[91,"충북","직할","서안성신진천#1 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","현수애자 절연성능진단 (중각도 철탑 3기)","2020-09-01 09:00","2020-09-02 18:00","2020-09-01 09:00","2020-09-02 18:00","매일"]
[92,"충북","직할","신진천S/S #1 M.Tr","'20~21년 직할 변전정비회사 총액공사","1, 2차 LA 하자점검 3차 LA 대체 2차 GIS 장기미동작 차단기 조작시험(예방) 옥외 기기조명등 교체 3차측 절연보강","2020-09-12 10:00","2020-09-13 18:00","2020-09-12 10:00","2020-09-13 18:00","연속"]
[93,"충북","청주","세종남청주#2 T/L","남청주S/S 345kV 장기사용 GIS 대체공사","345kV GIS 철거 및 설치 × 2CB","2020-09-07 08:00","2020-12-07 18:00","취소","취소","연속"]
[94,"충북","청주","세종남청주#2 T/L","2020-2021년 청주전력지사 송전정비회사 총액공사","항공도장 신옥천-세종#1 : 44, 49, 64, 68, 73호 (병가) 세종-남청주#2 : 9, 30호 애자교체 세종-남청주#2: 32, 46, 54, 55호","2020-09-07 08:00","2020-09-09 18:00","2020-09-07 08:00","2020-09-09 18:00","매일"]
[95,"충북","청주","세종남청주#1 T/L","2020-2021년 청주전력지사 송전정비회사 총액공사","항공도장 신옥천-세종#2 : 49, 54, 73(병가) 세종-남청주#1 : 30호","2020-09-02 08:00","2020-09-04 18:00","2020-09-02 08:00","2020-09-04 18:00","매일"]
[96,"충북","청주","남청주S/S #4 M.Tr","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV #4M.Tr 보통점검","2020-09-05 09:30","2020-09-06 18:00","2020-09-05 09:30","2020-09-06 18:00","연속"]
[97,"충북","청주","남청주S/S 345kV #1 BUS","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV CT집합반 교체공사","2020-09-19 09:00","2020-09-19 18:00","취소","취소","연속"]
[98,"충북","청주","신중부남청주#2 T/L","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV 신중부남청주#2T/L GIS 초기점검","2020-09-18 09:30","2020-09-18 18:00","2020-09-18 09:30","2020-09-18 18:00","연속"]
[99,"충북","청주","남청주S/S 345kV #2 BUS","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV CT집합반 교체공사","2020-09-20 09:00","2020-09-20 18:00","취소","취소","연속"]
[100,"충북","청주","신옥천세종#2 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 72BAY B/F반 교체공사","2020-09-01 08:00","2020-09-04 18:00","2020-09-01 08:00","2020-09-04 18:00","연속"]
[101,"충북","청주","신옥천북경남 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 72BAY B/F반 교체공사","2020-09-01 08:00","2020-09-04 18:00","2020-09-01 08:00","2020-09-04 18:00","연속"]
[102,"충북","청주","신옥천S/S #1 M.Tr","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 71BAY B/F반 교체공사","2020-09-07 08:00","2020-09-10 18:00","2020-09-07 08:00","2020-09-10 18:00","연속"]
[103,"충북","청주","신옥천세종#1 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 71BAY B/F반 교체 공사","2020-09-07 08:00","2020-09-10 18:00","2020-09-07 08:00","2020-09-10 18:00","연속"]
[104,"충북","청주","신옥천S/S 345kV #2 BUS","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 75BUS 모선보호반 교체공사","2020-09-14 10:00","2020-09-17 18:00","2020-09-14 10:00","2020-09-17 18:00","연속"]
[105,"충북","충주","신제천신충주#1 T/L","345kV 곤지암-신충주 등 4개T/L 전력선교체공사","- 전선교체 휴전작업 관련 4회선구간 병행휴전 - 본작업개소 345kV 곤지암-신충주T/L No.157~163","2020-09-04 07:00","2020-09-11 18:00","2020-09-04 07:00","2020-09-11 18:00","연속"]
[106,"충북","충주","신충주S/S STATCOM CB","신충주S/S STATCOM 냉각설비 초기점검 등","STATCOM 냉각설비 초기점검. STATCOM 345kV GIS(7071,7000) 및 345kV 변압기(A,B,C,예비) 하자점검.","2020-09-07 09:30","2020-09-11 18:00","2020-09-14 09:30","2020-09-18 18:00","연속"]
[107,"충북","충주","STATCOM M.Tr 1차 GIS","신충주S/S STATCOM 냉각설비 초기점검 등","STATCOM 냉각설비 초기점검. STATCOM 345kV GIS(7071,7000) 및 345kV 변압기(A,B,C,예비) 하자점검.","2020-09-07 09:30","2020-09-11 18:00","취소","취소","연속"]
[108,"충북","충주","곤지암신충주#2 T/L","345kV 곤지암-신충주 등 4개T/L 전력선교체공사","전선접소개소 해소 전력선교체공사","2020-09-08 07:00","2020-09-22 18:00","2020-09-08 07:00","2020-09-22 18:00","연속"]
[109,"충북","충주","신충주S/S #4 M.Tr","신충주S/S 154kV GIS 설치공사(전문)","신충주S/S 154kV Sh.C용 GIS설치 × 2CCT","2020-09-14 09:00","2020-09-25 18:00","2020-09-14 09:00","2020-09-25 18:00","연속"]
[110,"충북","충주","신충주S/S #3 M.Tr","20-21년 충주전력지사 변전정비 총액공사","신충주 #3M.Tr 변압기 1,2차 부싱절연유 채유, 7409-5 ES조작함 수분침투 관련 보수","2020-09-04 10:00","2020-09-04 18:00","2020-09-04 10:00","2020-09-04 18:00","연속"]
[111,"대전충남","대전","신계룡S/S 345kV CB 7100","신계룡S/S 345kV 7100 GIS CT 절연링 교체","신계룡S/S 345kV 7100 GIS CT 절연링 교체","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[112,"대전충남","서산","북당진현대제철 T/L","345kV 신송산분기T/L 건설사업","임시선로 구성 현대제철T/L(No.69 ~ No.71) 구간","2020-09-07 07:00","2020-09-10 19:00","2020-09-01 07:00","2020-09-04 19:00","연속"]
[113,"대전충남","서산","신당진개폐소현대제철 T/L","345kV 신송산분기T/L 건설공사","임시선로 구성 현대제철T/L(No.69 ~ No.71) 구간","2020-09-11 07:00","2020-09-14 19:00","2020-09-05 07:00","2020-09-08 19:00","연속"]
[114,"대전충남","서산","신당진S/S #3 M.Tr","'20년 장기 미동작 차단기 조작시험","신당진S/S 345kV #3 M.Tr 2차 6344 CB 조작시험","2020-09-28 10:00","2020-09-28 14:00","2020-09-28 10:00","2020-09-28 14:00","연속"]
[115,"대전충남","아산","신온양S/S 345kV #2 BUS","신온양S/S 345kV #2BUS측 부분방전 발생관련 내부점검","신온양S/S 345kV #2BUS측 부분방전 발생관련 내부점검","2020-09-22 09:00","2020-09-24 18:00","2020-09-22 09:00","2020-09-24 18:00","연속"]
[116,"대전충남","아산","청양신온양#2 T/L","[송전]345kV청양-신온양#2T/L 정밀점검","345kV청양-신온양#2T/L 84~116, 122~144, 145~149호 정밀점검","2020-09-14 08:00","2020-09-18 18:00","취소","취소","매일"]
[117,"대전충남","아산","신온양S/S 345kV CB 7571","2020년 신온양s/s 345kV GIS 정밀점검공사","- 차단기 차단부 가스회수 - 내부점검, 청소 진공후 가스주입 - 차단기 개폐타임측정","2020-09-02 09:00","2020-09-04 18:00","2020-09-02 09:00","2020-09-04 18:00","연속"]
[118,"대전충남","아산","신온양S/S 345kV CB 7572","2020년 신온양s/s 345kV GIS 정밀점검공사","- 차단기 차단부 가스회수 - 내부점검, 청소 진공후 가스주입 - 차단기 개폐타임측정","2020-09-07 09:00","2020-09-09 18:00","2020-09-07 09:00","2020-09-09 18:00","연속"]
[119,"대전충남","아산","신온양S/S 345kV CB 7500","2020년 신온양s/s 345kV GIS 정밀점검공사","- 차단기 차단부 가스회수 - 내부점검, 청소 진공후 가스주입 - 차단기 개폐타임측정","2020-09-10 09:00","2020-09-12 18:00","2020-09-10 09:00","2020-09-12 18:00","연속"]
[120,"대전충남","아산","신온양S/S 345kV CB 7772","2020년 신온양s/s 345kV GIS 정밀점검공사","- 차단기 차단부 가스회수 - 내부점검, 청소 진공후 가스주입 - 차단기 개폐타임측정","2020-09-22 09:00","2020-09-24 18:00","취소","취소","연속"]
[121,"대전충남","아산","신온양S/S 345kV CB 7600","2020년 신온양s/s 345kV GIS 정밀점검공사","- 차단기 차단부 가스회수 - 내부점검, 청소 진공후 가스주입 - 차단기 개폐타임측정","2020-09-14 09:00","2020-09-16 18:00","2020-09-14 09:00","2020-09-16 18:00","연속"]
[122,"대전충남","아산","신탕정S/S 345kV CB 7400","신탕정S/S 345kV #4M.Tr 증설공사","신탕정S/S 345kV #4M.Tr 증설공사","2020-09-07 07:00","2020-10-30 14:00","2020-09-07 07:00","2020-10-30 14:00","연속"]
[123,"대전충남","아산","신탕정S/S 345kV #2 BUS","신탕정S/S 345kV #4M.Tr 증설공사","신탕정S/S 345kV #4M.Tr 증설공사","2020-09-07 07:00","2020-09-11 14:00","2020-09-07 07:00","2020-09-11 14:00","연속"]
[124,"대전충남","청양","보령C/C 345kV #76 BUS","보령C/C 345kV 모선전압 불일치 관련 PT 점검","보령C/C 345kV 모선전압 불일치 관련 PT 점검","2020-09-21 15:00","2020-09-21 17:00","2020-09-21 15:00","2020-09-21 17:00","연속"]
[125,"대전충남","청양","신보령TP보령CC T/L","보령C/C 345kV 신보령연락T/L GIS 과열개소 점검","보령C/C 345kV 신보령연락T/L GIS 과열개소 점검","2020-09-19 09:00","2020-09-19 13:00","취소","취소","연속"]
[126,"대전충남","청양","보령C/C 345kV #70 BUS","보령C/C 345kV 모선전압 불일치 관련 PT 점검","보령C/C 345kV 모선전압 불일치 관련 PT 점검","2020-09-21 09:00","2020-09-21 11:00","2020-09-21 09:00","2020-09-21 11:00","연속"]
[127,"대전충남","청양","보령C/C 345kV #75 BUS","보령C/C 345kV 모선전압 불일치 관련 PT 점검","보령C/C 345kV 모선전압 불일치 관련 PT 점검","2020-09-21 13:00","2020-09-21 15:00","2020-09-21 13:00","2020-09-21 15:00","연속"]
[128,"대전충남","청양","보령C/C 345kV #71 BUS","보령C/C 345kV 모선전압 불일치 관련 PT 점검","보령C/C 345kV 모선전압 불일치 관련 PT 점검","2020-09-21 11:00","2020-09-21 13:00","2020-09-21 11:00","2020-09-21 13:00","연속"]
[129,"대전충남","청양","청양보령CC T/L","보령C/C 345kV 청양-보령복합T/L GIS 과열개소 점검","보령C/C 345kV 청양-보령복합T/L GIS 과열개소 점검","2020-09-19 13:00","2020-09-19 18:00","취소","취소","연속"]
[130,"대전충남","청양","청양군산#2 T/L","청양S/S #73BAY B/F 대체공사","청양S/S #73BAY B/F 대체공사","2020-09-21 09:00","2020-09-25 18:00","취소","취소","연속"]
[131,"대전충남","청양","청양신탕정 T/L","청양S/S #73BAY B/F 대체공사","청양S/S #73BAY B/F 대체공사","2020-09-21 09:00","2020-09-25 18:00","취소","취소","연속"]
[132,"전북","군산","새만금S/S #3 M.Tr","새만금S/S 종합예방진단시스템 구축공사","새만금S/S #3M.Tr 종합예방진단시스템 구축공사 - OLTC센서 설치부 실측","2020-09-01 13:00","2020-09-01 15:00","2020-09-01 13:00","2020-09-01 15:00","연속"]
[133,"전북","군산","새만금S/S #2 M.Tr","새만금S/S 종합예방진단시스템 구축공사","새만금S/S #2M.Tr 종합예방진단시스템 구축공사 - OLTC센서 설치부 실측","2020-09-01 10:00","2020-09-01 13:00","2020-09-01 10:00","2020-09-01 13:00","연속"]
[134,"전북","김제","신김제S/S #1 M.Tr","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (MAIN 교체)","2020-09-01 09:00","2020-09-23 18:00","2020-09-01 09:00","2020-09-23 18:00","연속"]
[135,"전북","직할","신남원광양#1 T/L","신남원S/S GAS 누기보수공사(7500)","신남원S/S GAS 누기보수공사 [휴전개소 : 신남원-광양#1T/L, #75BUS] [작업개소 : 7500(A/B/C)]","2020-09-10 09:00","2020-09-21 09:00","2020-09-10 09:00","2020-09-21 09:00","연속"]
[136,"전북","직할","신남원광양#2 T/L","신남원S/S GAS 누기보수공사(7671/7661)","신남원S/S GAS 누기보수공사 [휴전개소 : 신남원-광양#2T/L, #70BUS] [작업개소 : 7671(A/B/C), 7661(B)]","2020-09-21 09:00","2020-10-19 18:00","2020-09-21 09:00","2020-10-19 18:00","연속"]
[137,"전북","직할","신남원S/S 345kV #1 BUS","신남원S/S GAS 누기보수공사(#70BUS)","신남원S/S GAS 누기보수공사 [휴전개소 : #70BUS] [작업개소] - 7271/7200(04/07~04/27) - 7471(05/26~05/29) - 7371(05/30~06/02) - 7671/7661(06/15~06/28)","2020-09-25 09:00","2020-10-19 18:00","2020-09-25 09:00","2020-10-19 18:00","연속"]
[138,"전북","직할","신남원S/S 345kV #2 BUS","신남원S/S GAS 누기보수공사(#75BUS)","신남원S/S GAS 누기보수공사 [휴전개소 : #75BUS] [작업개소] - 7600(04/28~05/21) - 7272(05/02~05/13) - 7352/7452(05/14~05/25) - 7500(06/03~06/14)","2020-09-09 09:00","2020-09-24 18:00","2020-09-09 09:00","2020-09-24 18:00","연속"]
[139,"전북","직할","신남원신광주#1 T/L","`20~`21년 전북 직할 변전정비회사 총액공사","신남원S/S 7771GIS 보통점검 및 노후 단자대 교체","2020-09-01 09:00","2020-09-02 09:00","2020-09-01 09:00","2020-09-02 09:00","연속"]
[140,"전북","직할","신남원신광주#2 T/L","`20~`21년 전북 직할 변전정비회사 총액공사","신남원S/S 7871, 7800GIS 보통점검 및 노후 단자대 교체","2020-09-03 09:00","2020-09-04 09:00","2020-09-03 09:00","2020-09-04 09:00","연속"]
[141,"광주전남","강진","신강진S/S #2 M.Tr","20-21년 강진전력지사 변전정비회사 총액공사","○ #2M.Tr 1차 부싱 절연열화 측정 ○ #2M.Tr 2차 LA A,B,C 초기점검 ○ #2M.Tr 3차 BUS PT A,B,C 하자점검","2020-09-22 09:00","2020-09-22 18:00","2020-09-17 09:00","2020-09-17 18:00","연속"]
[142,"광주전남","강진","신강진S/S #1 M.Tr","20-21년 강진전력지사 변전정비회사 총액공사","○ #1M.Tr 1차 부싱 절연열화 측정 ○ #1M.Tr 3차 VCB 대체","2020-09-21 09:00","2020-09-21 18:00","2020-09-16 09:00","2020-09-16 18:00","연속"]
[143,"광주전남","광주","신광주S/S 345kV CB 7171","2020년 신광주S/S 345kV GIS 정밀점검","신광주S/S 345kV 신광주-한빛#1T/L 7171CB 정밀점검","2020-09-21 09:30","2020-09-24 18:00","2020-09-21 09:30","2020-09-24 18:00","연속"]
[144,"광주전남","광주","신광주S/S 345kV CB 7271","2020년 신광주S/S 345kV GIS 정밀점검","신광주S/S 345kV 신광주-한빛#2T/L 7271CB 정밀점검","2020-09-14 09:30","2020-09-17 18:00","2020-09-14 09:30","2020-09-17 18:00","연속"]
[145,"광주전남","광주","신광주신화순#1 T/L","20년 변전정비회사 총액공사(LA 대체)","-(신광주S/S) 신광주-신화순#1T/L 345kV LA 대체 -(신화순S/S) 7771CB Dashpot 누유 보수","2020-09-21 09:00","2020-09-22 18:00","2020-09-27 09:00","2020-09-28 18:00","연속"]
[146,"광주전남","광주","신광주S/S 345kV #2 BUS","2020∼21년 광주전력지사 변전정비회사 총액공사","345kV #75BUS 모선보호반 교체","2020-09-14 09:00","2020-09-18 18:00","취소","취소","연속"]
[147,"광주전남","광주","신광주S/S 345kV #1 BUS","2020∼21년 광주전력지사 변전정비회사 총액공사","345kV #70BUS 모선보호반 교체","2020-09-07 09:00","2020-09-11 18:00","취소","취소","연속"]
[148,"광주전남","순천","신남원광양#2 T/L","광양S/S 362kV GIS 용량 대체공사","○ 광양S/S 362kV GIS 용량 대체 안전이격 확보 - 7151DS 및 #70BUS(71Bay) M-BUS 대체","2020-09-21 09:00","2020-09-28 09:00","취소","취소","연속"]
[149,"광주전남","순천","광양S/S 345kV CB 7471","20-21년 순천전력지사 변전정비회사 총액공사","여수T/P : 광양-여수T/PT/L 현수애자 교체 및 광양-여수T/PT/L CVT(A,B,C)상 초기 및 LA(A,B,C)상 보통점검 광양S/S : 광양S/S 7471 GIS 초기점검 및 광양-여수T/PT/L LA(A,B,C)상 및 CVT 보통점검","2020-09-01 09:00","2020-09-02 18:00","2020-09-01 09:00","2020-09-02 18:00","연속"]
[150,"광주전남","순천","광양S/S 345kV #70 BUS","광양S/S 362kV GIS 용량대체공사","○ 광양S/S 362kV GIS 용량대체공사 - #70 BUS 및 DS(71~73BAY) 대체(50kA → 63kA)","2020-09-03 09:00","2020-10-16 18:00","2020-09-03 09:00","2020-10-16 18:00","연속"]
[151,"광주전남","순천","광양율촌CC T/L","광양S/S 362kV GIS 용량 대체공사","○ 광양S/S 362kV GIS 용량 대체 안전이격 확보 - 7351DS 및 #70BUS(73Bay) M-BUS 대체","2020-09-07 09:00","2020-09-14 09:00","2020-09-07 09:00","2020-09-14 09:00","연속"]
[152,"광주전남","순천","광양하동TP#2 T/L","20-21년 순천전력지사 변전정비회사 총액공사","광양S/S 하동TP-광양#2T/L 7671,7600 타임측정 및 LA(A,B,C)상 초기점검 및 절연열화측정","2020-09-14 09:00","2020-09-14 18:00","취소","취소","연속"]
[153,"광주전남","순천","광양하동TP#1 T/L","20-21년 순천전력지사 변전정비회사 총액공사","광양S/S 하동TP-광양#1T/L 7571,7500 타임측정 및 LA(A,B,C)상 초기점검 및 절연열화측정 CVT(A,B,C)상 대체","2020-09-15 09:00","2020-09-15 18:00","취소","취소","연속"]
[154,"광주전남","순천","신남원광양#1 T/L","광양S/S 362kV GIS 용량 대체공사","○ 광양S/S 362kV GIS 용량 대체 안전이격 확보 - 7251DS 및 #70BUS(72Bay) M-BUS 대체","2020-09-14 09:00","2020-09-21 09:00","취소","취소","연속"]
[155,"광주전남","순천","여수T/P #1 Tie-Tr","20-21년 순천전력지사 변전정비회사 총액공사","여수화력S/Y #1M.Tr 1차 GIS 7172, 7100 도블측정, 타임측정, 2차 GIS 보통, 3차 VCB 4184 타임, 1,2차 LA (A,B,C)상 대체, 3차GPT 초기","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[156,"광주전남","순천","여수T/P 345kV #1 BUS","여수화력S/Y #4M.Tr 및 SW 증설공사","345kV #4M.Tr 및 광양CC-여수TP #1,2T/L 증설","2020-09-01 09:00","2020-09-03 18:00","2020-09-01 09:00","2020-09-03 18:00","연속"]
[157,"광주전남","순천","여수T/P 345kV #2 BUS","여수화력S/Y #4M.Tr 및 SW 증설공사","345kV #4M.Tr 및 광양CC-여수TP #1,2T/L 증설","2020-09-07 09:00","2020-09-09 18:00","2020-09-07 09:00","2020-09-09 18:00","연속"]
[158,"광주전남","순천","율촌CC여수TP T/L","345kV 율촌C/C-여수T/P T/L 정밀점검","20년도 가공송전 순시점검 위탁공사 - 율촌C/C분기 T/L 정밀점검 : No.1~11호(11기)","2020-09-18 08:00","2020-09-18 18:00","취소","취소","연속"]
[159,"대구","경산","신경산S/S #2 M.Tr","2020~21년 경산변전협력 총액공사","2차측하자점검,기계적경보분리","2020-09-11 09:30","2020-09-11 18:00","2020-09-11 09:30","2020-09-11 18:00","연속"]
[160,"대구","경산","신경산S/S #3 M.Tr","2020~21년 경산변전협력 총액공사","2차측하자점검,기계적경보분리","2020-09-15 09:30","2020-09-15 18:00","2020-09-15 09:30","2020-09-15 18:00","연속"]
[161,"대구","경산","신경산S/S #1 M.Tr","2020~21년 경산변전협력 총액공사","B/F반대체작업","2020-09-21 09:30","2020-09-25 18:00","2020-09-21 09:30","2020-09-25 18:00","연속"]
[162,"대구","달성","고령S/S #2 M.Tr","고령S/S 345kV #2M.Tr A,C상 정밀점검","고령S/S 345kV #2M.Tr A,C상 정밀점검","2020-09-14 09:00","2020-09-18 18:00","2020-09-14 09:00","2020-09-18 18:00","연속"]
[163,"대구","달성","대구S/S #3 M.Tr","대구S/S 345kV #3M.Tr 96P,96D 회로보완","대구S/S 345kV #3M.Tr 96P,96D 회로보완","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[164,"대구","달성","대구S/S #1 M.Tr","대구S/S 345kV #1M.Tr 96P,96D 회로보완","대구S/S 345kV #1M.Tr 96P,96D 회로보완","2020-09-22 09:00","2020-09-22 18:00","2020-09-29 09:00","2020-09-29 18:00","연속"]
[165,"대구","칠곡","북대구S/S 345kV #1 BUS","북대구S/S #70BUS 모선보호반 교체작업","북대구S/S #70BUS 모선보호반 교체작업","2020-09-07 09:30","2020-09-11 18:00","2020-09-07 09:30","2020-09-11 18:00","연속"]
[166,"대구","칠곡","서대구S/S #2 M.Tr","서대구S/S 154kV 옥외철구 설비 GIS화 공사(토목)","전력구 굴착 시 안전망 시공을 위한 H파일 항타 안전이격 확보","2020-09-07 07:30","2020-09-07 18:00","2020-09-03 08:00","2020-09-03 18:00","연속"]
[167,"대구","칠곡","서대구S/S #4 M.Tr","서대구S/S #4 M.Tr 기계적보호장치 회로보완","서대구S/S #4 M.Tr 기계적보호장치 회로보완","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[168,"대구","포항","신영일S/S #3 M.Tr","신영일S/S 75B/F PNL 대체작업","신영일S/S 75B/F PNL 대체작업","2020-09-07 09:00","2020-09-11 18:00","2020-09-07 09:00","2020-09-11 18:00","연속"]
[169,"대구","포항","선산신포항 T/L","2020~21년도 직할 가공송전 정비회사 총액공사","No.138~139 애자련보강, (안전확보) No.95,102,132,133송전철탑 추락방지시설 설치","2020-09-18 08:00","2020-09-18 18:00","2020-09-18 08:00","2020-09-18 18:00","연속"]
[170,"대구","포항","신포항S/S #2 M.Tr","신포항S/S #2M.Tr 96P 커버 설치 작업","신포항S/S #2M.Tr 96P 커버 설치 작업","2020-09-10 09:00","2020-09-10 18:00","2020-09-10 09:00","2020-09-10 18:00","연속"]
[171,"대구","포항","신포항북대구 T/L","2020~21년도 직할 가공송전 정비회사 총액공사","No.138~139 애자련보강, (안전확보) No.95,102,132,133송전철탑 추락방지시설 설치","2020-09-17 08:00","2020-09-17 18:00","2020-09-17 08:00","2020-09-17 18:00","연속"]
[172,"대구","포항","신포항S/S #1 M.Tr","신포항S/S 154kV 옥외철구 설비 GIS화 공사","- 인출 2단 POST측 상부계탑 대체 및 상부 BEAM 1기 철거 - 변압기 보호반 회로보완 및 제어케이블 포결선 - 변압기 2차측 옥외철구에서 GIS로 부하이양 (GIS로 가압) - 변압기 2차측 상부모선 및 금구류 철거 - 변압기 2차측 모선배선, 가공지선 대체 및 수직분기선 GIS부싱 연결 - CB, DS, 기기가대, ILC PNL, 제어케이블 철거 등","2020-09-24 08:00","2020-09-27 18:00","2020-09-22 09:00","2020-09-27 18:00","연속"]
[173,"경북","구미","선산S/S 345kV 예비 M.Tr CB","선산S/S 345kV 예비변압기 1차 부싱 교체공사","- TEST TAP 누유관련 부싱 교체공사 - 주기기제작사(현대일렉트릭) 시행","2020-09-14 09:00","2020-09-16 18:00","취소","취소","연속"]
[174,"경북","구미","선산S/S #4 M.Tr","77BAY BF PNL 교체공사","77BAY BF PNL 교체공사","2020-09-07 09:00","2020-09-09 18:00","2020-09-07 09:00","2020-09-09 18:00","연속"]
[175,"경북","영주","신영주한울NP2#2 T/L","345kV 신영주-한울NP2T/L 전선접속개소 전력선 교체공사","가. 공사구간 : №99-105, 174-180호 나. 공사수량 : ACSR 480㎟(Cardinal) 10.14 C-㎞ 교체","2020-09-10 07:00","2020-09-18 18:00","2020-09-10 07:00","2020-09-18 18:00","연속"]
[176,"경북","영주","신영주한울NP2#1 T/L","345kV 신영주-한울NP2T/L 전선접속개소 전력선 교체공사","가. 공사구간 : №99-105, 174-180호 나. 공사수량 : ACSR 480㎟(Cardinal) 10.14 C-㎞ 교체","2020-09-01 07:00","2020-09-09 18:00","2020-09-01 07:00","2020-09-09 18:00","연속"]
[177,"경북","영주","신영주S/S #3 M.Tr","신영주S/S 154kV 현대화관련 전력구공사","신영주S/S 154kV 옥외철구설비 현대화사업 전력구공사 - 맨홀 설치 관련 가시설 시공 - 대상 : 345kV #3 M.Tr","2020-09-28 09:00","2020-09-29 18:00","2020-09-28 09:00","2020-09-29 18:00","연속"]
[178,"경북","영주","신한울한울#1 T/L","345kV 신한울-한울연락T/L 철탑안전도 검토 용역","345kV 신한울-한울연락T/L No.1, 3호 철탑안전도 검토 및 현장실측","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[179,"경북","영주","신한울한울#2 T/L","2020-21년 영주전력지사 변전정비회사 총액공사","- YPP 계전기 성능개선 - #2M.Tr B-2상 권선온도계 교체 - B-2상 중압 부싱 접지선 과열 및 고압권선 온도 상한 경보 조치 - B-2상 탭가드 히터 불량 조치 - A-1상 탭가드 온도센서 불량 조치 - M.Tr 원격제어반 C-1상 TPI 교체 - C-1상 4그룹 B상 모터 불량 조치","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]
[180,"경북","영주","한울1NP한울2NP#2 T/L","YPP 계전기 성능개선","- YPP 계전기 성능개선","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[181,"부산울산","동부산","고리N/P 345kV CB 7B71","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 7B71 CB C상 유압펌프 이음관련 불량조치","2020-09-28 09:00","2020-09-28 15:00","2020-09-28 09:00","2020-09-28 15:00","연속"]
[182,"부산울산","동부산","고리N/P 345kV CB 7F00","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 7F00 CB A상 CB카운터 불량조치","2020-09-28 15:00","2020-09-28 17:00","2020-09-28 15:00","2020-09-28 17:00","연속"]
[183,"부산울산","동부산","신양산S/S #1 M.Tr","[철거1차] 345kV 신양산S/S 현대화 일반공사","#1M.Tr 2차측 옥외철구 설비 철거","2020-09-21 08:00","2020-09-25 18:00","2020-09-21 08:00","2020-09-25 18:00","연속"]
[184,"부산울산","서부산","신김해신녹산#2 T/L","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해-신녹산#2T/L CB(7371) 시험가압","2020-09-24 17:00","2020-09-24 18:00","2020-09-24 17:00","2020-09-24 18:00","연속"]
[185,"부산울산","서부산","신녹산S/S 345kV CB 7371","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해-신녹산#2T/L CB(7371) 정밀점검","2020-09-21 09:00","2020-09-24 18:00","2020-09-21 09:00","2020-09-24 18:00","연속"]
[186,"부산울산","서부산","신녹산S/S 345kV CB 7300","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해#2T/L-#3M.Tr 1차 TIE CB(7300) 정밀점검","2020-09-25 09:00","2020-09-28 18:00","2020-09-25 09:00","2020-09-28 18:00","연속"]
[187,"부산울산","서부산","신김해신녹산#1 T/L","'20-'21년 서부산 가공송전 정비회사 총액공사","추락방지장치 설치 신김해-신녹산T/L 40~41호","2020-09-22 07:00","2020-09-22 12:00","2020-09-22 07:00","2020-09-22 12:00","연속"]
[188,"부산울산","서부산","신김해신녹산#2 T/L","'20-'21년 서부산 가공송전 정비회사 총액공사","추락방지장치 설치 및 소도체이도조정","2020-09-22 12:00","2020-09-24 16:00","2020-09-22 12:00","2020-09-24 16:00","연속"]
[189,"부산울산","서부산","신김해신녹산#2 T/L","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해#2T/L-#3M.Tr 1차 TIE CB(7300) 시험가압","2020-09-28 17:00","2020-09-28 18:00","2020-09-28 17:00","2020-09-28 18:00","연속"]
[190,"부산울산","울산","신온산S/S #4 M.Tr","20-21년 변전정비회사 총액공사","- 3차측 동우제 PT 특별점검","2020-09-29 09:00","2020-09-29 18:00","2020-09-29 09:00","2020-09-29 18:00","연속"]
[191,"부산울산","울산","신온산울산TP T/L","345kV 신울산복합-북부산T/L 건설공사","작업내용 : 345kV 신온산-울산TP T/L 본선로 구성(전선이동) 154kV 신온산-성암#2 본선로 구성(전선이동)","2020-09-10 07:00","2020-09-21 18:00","2020-09-10 07:00","2020-09-21 18:00","연속"]
[192,"부산울산","울산","북부산신온산 T/L","345kV 신울산복합-북부산T/L 건설공사","작업내용 : 345kV 북부산-신온산T/L 임시선로 구성(전선이동) 및 345kV 북부산-신온산T/L 22호 철탑 바디보강 및 암교체 154kV 신온산-성암#1 본선로 구성(전선이동)","2020-09-22 07:00","2020-09-29 18:00","2020-09-22 07:00","2020-09-29 18:00","연속"]
[193,"부산울산","울산","북부산신온산 T/L","345kV 신울산복합-북부산T/L 건설공사","작업내용 : 345kV 북부산-신온산T/L 임시선로 구성(전선이동) 154kV 신온산-성암#1 본선로 구성(전선이동)","2020-09-01 07:00","2020-09-09 18:00","2020-09-01 07:00","2020-09-09 18:00","연속"]
[194,"부산울산","울산","울산C/C 345kV CB 7100","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS 도킹연결 작업 인접구간휴전","2020-09-25 09:00","2020-10-25 18:00","2020-10-05 09:00","2020-11-02 18:00","연속"]
[195,"부산울산","울산","울산C/C 345kV #1 BUS","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 전 모선마감처리 휴전","2020-09-25 09:00","2020-09-26 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[196,"부산울산","울산","울산C/C 345kV CB 7A00","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS 도킹연결 작업 인접구간휴전","2020-09-25 09:00","2020-10-25 18:00","2020-10-05 09:00","2020-11-02 18:00","연속"]
[197,"부산울산","울산","울산C/C #3 Tie-Tr","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 전 모선마감 처리 후 시험가압 1H","2020-09-26 09:00","2020-09-26 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[198,"부산울산","울산","북부산울산TP T/L","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 전 모선마감 처리 후 시험가압1H","2020-09-23 18:00","2020-09-23 19:00","취소","취소","연속"]
[199,"부산울산","울산","울주S/S #2 M.Tr","20-21년 변전정비회사 총액공사","- 3차측 동우제 PT 특별점검 - 방호벽 도장","2020-09-29 09:00","2020-09-29 18:00","2020-09-29 09:00","2020-09-29 18:00","연속"]
[200,"부산울산","울산","울주S/S #4 M.Tr","20-21년 변전정비회사 총액공사","- M.Tr 보호반 대체 - 방호벽 도장, 등작업 - 1,2차 LA 대체","2020-09-07 09:00","2020-09-11 18:00","2020-09-07 09:00","2020-09-11 18:00","연속"]
[201,"부산울산","울산","울주월성NP#2 T/L","2020-21년 울산전력지사 변전협력회사 총액공사","-CVT 대체","2020-09-28 09:00","2020-09-28 18:00","2020-09-28 09:00","2020-09-28 18:00","연속"]
[202,"부산울산","울산","울주고리NP#2 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","345kV 울주-고리 #2 T/L 스페이서 간격조정 ○ 대상 : 75~91호 (17기)","2020-09-21 08:00","2020-09-23 18:00","2020-09-21 08:00","2020-09-23 18:00","연속"]
[203,"부산울산","울산","울주고리NP#1 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","345kV 울주-고리 #1 T/L 스페이서 간격조정 ○ 대상 : 75~91호 (17기)","2020-09-24 08:00","2020-09-26 18:00","2020-09-24 08:00","2020-09-26 18:00","연속"]
[204,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(1차)-시험가압선로","신김해S/S 154kV 장기사용GIS 교체공사(1차) 대상 : 신김해-지사#2, 신김해-주촌#1T/L GIS","2020-09-12 12:00","2020-09-12 18:00","2020-09-12 12:00","2020-09-12 18:00","연속"]
[205,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(1차)-시험가압선로","신김해S/S 154kV 장기사용GIS 교체공사(1차) 대상 : 신김해-지사#2, 신김해-주촌#1T/L GIS","2020-09-19 18:00","2020-09-20 18:00","2020-09-19 18:00","2020-09-20 18:00","연속"]
[206,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(1차)-시험가압선로","신김해S/S 154kV 장기사용GIS 교체공사(1차) 대상 : 신김해-지사#2, 신김해-주촌#1T/L GIS","2020-09-25 18:00","2020-09-27 18:00","2020-09-25 18:00","2020-09-27 18:00","연속"]
[207,"경남","직할","창원삼천포TP#1 T/L","창원-삼천포#1 T/L 송전선로 정밀점검","창원-삼천포#1L 송전선로 정밀점검(103~183)","2020-09-01 08:00","2020-09-04 17:00","2020-09-01 08:00","2020-09-14 17:00","매일"]
[208,"경남","직할","신김해창원#2 T/L","신김해-창원#2T/L 송전선로 정밀점검","신김해-창원#2 송전선로 정밀점검 (8~52호)","2020-09-28 08:00","2020-09-29 17:00","취소","취소","매일"]
[209,"경남","직할","신김해창원#2 T/L","신김해-창원#2T/L 송전선로 정밀점검","신김해-창원#2 송전선로 정밀점검 (8~52호)","2020-09-22 08:00","2020-09-25 17:00","2020-09-22 08:00","2020-09-29 17:00","매일"]
[210,"경남","직할","창원삼천포TP#1 T/L","창원-삼천포#1 T/L 송전선로 정밀점검","창원-삼천포#1L 송전선로 정밀점검(103~183)","2020-09-14 08:00","2020-09-14 17:00","취소","취소","매일"]
[211,"경남","직할","창원삼천포TP#1 T/L","창원-삼천포#1 T/L 송전선로 정밀점검","창원-삼천포#1L 송전선로 정밀점검(103~183)","2020-09-07 08:00","2020-09-11 17:00","취소","취소","매일"]
[212,"경남","진주","의령산청양수#1 T/L","산청P/P 의령-산청양수#1T/L-#1, 2M.Tr 1차 CB 조작시험","산청P/P 의령-산청양수#1T/L - #1, 2M.Tr 1차 CB 조작시험 병행 : 의령, 산청P/P 의령-산청양수#1T/L PT, LA 보통점검","2020-09-28 10:00","2020-09-29 18:00","2020-09-28 10:00","2020-09-29 18:00","연속"]
[213,"경남","통영","고성하이T/P 345kV CB 7100","345kV 고성하이S/Y 건설공사","G1호기 계통병입 준비작업","2020-09-07 09:00","2020-10-05 18:00","2020-09-07 09:00","2020-10-05 18:00","연속"]
[214,"경남","통영","고성하이T/P 345kV CB 7172","345kV 고성하이S/Y 건설공사","G1호기 계통병입 준비작업","2020-09-07 09:00","2020-10-05 18:00","2020-09-07 09:00","2020-10-05 18:00","연속"]
[215,"경남","통영","삼천포T/P 345kV CB 7571","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[216,"경남","통영","창원삼천포TP#1 T/L","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[217,"경남","통영","신마산삼천포화력#1 T/L","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[218,"경남","통영","신마산삼천포화력#2 T/L","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-15 09:00","2020-09-29 18:00","2020-09-15 09:00","2020-09-29 18:00","연속"]
[219,"경남","통영","삼천포T/P 345kV CB 7272","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[220,"경남","통영","삼천포T/P 345kV CB 7400G","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[221,"경남","통영","삼천포T/P 345kV CB 7472G","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[222,"경남","통영","삼천포T/P 345kV CB 7A00G","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[223,"경남","통영","삼천포T/P 345kV CB 7A72G","345kV 삼천포, 신고성S/S 차단기 용량대체공사","인출변경작업","2020-09-01 09:00","2020-09-14 18:00","2020-09-01 09:00","2020-09-14 18:00","연속"]
[224,"부산울산",null,"고리N/P #2 Tie-Tr CB","강압변압기 #2 정밀점검 및 방열기 교체공사 ＊조작차단기 : 7D71, 7D00","신고리 345kV 변전소내 강압변압기 No.2 정밀점검 및 방열기 교체공사","2020-09-01 13:00","2020-09-11 18:00","2020-09-01 13:00","2020-09-11 18:00","연속"]
[225,"부산울산",null,"고리N/P #1 Tie-Tr CB","강압변압기 #2 정밀점검 및 방열기 교체공사 ＊조작차단기 : 7671, 7600","신고리 345kV 변전소내 강압변압기 No.1 정밀점검 및 방열기 교체공사","2020-09-14 09:00","2020-09-25 18:00","2020-09-14 09:00","2020-09-25 18:00","연속"]
[226,"경북",null,"한울N/P #6호기 대기보조변압기 CB (7B00, 7B72)","6호기 11차 계획예방정비 * 조작차단기 : CB 7B00, 7B72","○ 대기보조변압기 일반점검","2020-09-10 16:00","2020-09-25 14:00","2020-09-10 16:00","2020-09-25 14:00","연속"]
[227,"경북",null,"한울N/P #6호기 주변압기 CB (7C00, 7C72)","6호기 11차 계획예방정비 * 조작차단기 : CB 7C00, 7C72","○ 소내전원 절체(UAT→SAT)시험","2020-09-28 13:00","2020-09-28 18:00","2020-09-28 13:00","2020-09-28 18:00","연속"]
[228,"대구",null,"월성N/P #4호기 기동용변압기 CB (7800, 7872)","월성4호기 17차 O/H 중 정전작업 및 전원절체 * 조작차단기 : 7800, 7872","○ 소내전원절체시험","2020-09-20 09:00","2020-09-25 23:59","2020-09-20 09:00","2020-09-25 23:59","연속"]
[229,"대구",null,"월성N/P #2호기 주변압기 CB (7300, 7372)","월성2호기 19차 O/H 중 주변압기 점검 * 조작차단기 : 7300, 7372","주변압기 일반점검 등","2020-09-16 09:00","2020-10-19 18:00","2020-09-16 09:00","2020-10-19 18:00","연속"]
[230,"대구",null,"월성N/P #4 주변압기CB(7772, 7700)","월성4호기 17차 O/H 중 전원절체 및 동기병입 회로시험 * 조작차단기 : CB 7700, 7772","○ 발전기 동기병입 회로시험","2020-09-24 00:01","2020-09-27 18:00","2020-09-24 00:01","2020-09-27 18:00","연속"]
[231,"경기",null,"평택복합 #6G/T 주변압기 CB (7800, 7871)","변압기 정밀점검","변압기 정밀점검","2020-09-03 08:30","2020-09-18 18:00","2020-09-03 08:30","2020-09-18 18:00","연속"]
[232,"경기",null,"평택복합 #2S/T 주변압기 CB (7800, 7872)","변압기 정밀점검","변압기 정밀점검","2020-09-19 08:30","2020-09-28 18:00","2020-09-19 08:30","2020-09-28 18:00","연속"]
[233,"대전충남",null,"보령화력 #3,4호기 기동변압기 CB (7372, 7300)","기동변압기 정기점검 및 보호계전기 시험","기동변압기 정기점검 및 보호계전기 시험","2020-09-07 10:00","2020-09-11 17:00","2020-09-07 10:00","2020-09-11 17:00","연속"]
[234,"인천",null,"인천복합 #5,6G/T 주변압기 CB (7B00, 7B71)","변압기, GCB 점검 및 정기검사","변압기, GCB 점검 및 정기검사","2020-09-24 09:00","2020-10-21 18:00","2020-09-24 09:00","2020-10-21 18:00","연속"]
[235,"인천",null,"인천복합 #3S/T 주변압기 CB (7B00, 7B73)","변압기, GCB 점검 및 정기검사","변압기, GCB 점검 및 정기검사","2020-09-24 09:01","2020-10-21 18:01","2020-09-24 09:00","2020-10-21 18:00","연속"]

{"sheet":"154송부","index":2,"n_rows":529,"n_cols":11,"rows_kept":529,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 9월 휴전계획서"]
["154kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","성동","화양광장 T/L","154kV 화양-광장T/L 정밀점검","- No.3등 철탑21기 정밀점검","2020-09-11 09:00","2020-09-11 18:00","2020-09-11 09:00","2020-09-11 18:00","연속"]
[2,"서울","성동","광장S/S 154kV CB 6100","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-21 10:00","2020-09-21 13:00","취소","취소","연속"]
[3,"서울","성동","천호구의#1 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-21 14:00","2020-09-21 17:30","취소","취소","연속"]
[4,"서울","성동","마장용두 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-22 10:00","2020-09-22 13:00","2020-09-23 10:00","2020-09-23 13:00","연속"]
[5,"서울","성동","금오상계#1 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-23 10:00","2020-09-23 13:00","2020-09-23 10:00","2020-09-23 13:00","연속"]
[6,"서울","성동","금오상계#2 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-23 14:00","2020-09-23 17:30","2020-09-23 14:00","2020-09-23 17:30","연속"]
[7,"서울","성동","성동S/S 154kV SEC CB 65660","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-29 15:00","2020-09-29 17:30","2020-09-29 15:00","2020-09-29 17:30","연속"]
[8,"서울","성동","성동S/S 154kV SEC CB 60610","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-29 13:00","2020-09-29 15:00","2020-09-29 13:00","2020-09-29 15:00","연속"]
[9,"서울","성동","성동S/S 154kV CB 6200","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-29 11:00","2020-09-29 13:00","2020-09-29 11:00","2020-09-29 13:00","연속"]
[10,"서울","성동","성동휘경#2 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-28 14:00","2020-09-28 17:30","2020-09-28 14:00","2020-09-28 17:30","연속"]
[11,"서울","성동","성동S/S 154kV CB 6100","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-09-29 09:00","2020-09-29 11:00","2020-09-29 09:00","2020-09-29 11:00","연속"]
[12,"서울","성동","성수뚝도#2 T/L","'20년 성동P/O 노후 보호배전반 교체공사","성수, 뚝도S/S 154kV 성수뚝도#2T/L 보호배전반 노후대체","2020-09-14 10:00","2020-09-17 17:00","취소","취소","연속"]
[13,"서울","성동","성수뚝도#1 T/L","'20년 성동P/O 노후 보호배전반 교체공사","성수, 뚝도S/S 154kV 성수뚝도#1T/L 보호배전반 노후대체","2020-09-07 10:00","2020-09-10 17:00","취소","취소","연속"]
[14,"서울","중부","동빙고S/S 154kV #65 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검(#65BUS DS 점검)","2020-09-22 14:00","2020-09-23 18:00","2020-09-22 14:00","2020-09-23 18:00","연속"]
[15,"서울","중부","순화동빙고 T/L","154kV 순화동빙고T/L 케이블 교체공사","■ 선로명 : 154kV 순화동빙고T/L ■ 선종 및 길이 : 154kV OF 1,200㎟ × 1회선 - 2.14km → XLPE 1,200㎟ × 1회선 - 2.14km ■ 포설 및 접속 : 포설 7구간, 접속 8개소 (중간7개소, 종단1개소)","2020-09-01 09:00","2020-11-20 18:00","2020-09-07 09:00","2020-11-20 18:00","연속"]
[16,"서울","중부","용산동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검(시험가압)","2020-09-23 17:00","2020-09-23 18:00","2020-09-23 17:00","2020-09-23 18:00","연속"]
[17,"서울","중부","동빙고S/S 154kV #65 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #3M.Tr 1차 GIS 정밀점검(#65BUS DS 점검)","2020-09-16 00:09","2020-09-17 14:00","2020-09-16 00:00","2020-09-17 14:00","연속"]
[18,"서울","중부","동빙고S/S 154kV #60 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검(#60BUS DS 점검 및 시험가압)","2020-09-21 09:00","2020-09-22 14:00","2020-09-21 09:00","2020-09-22 14:00","연속"]
[19,"서울","중부","용산동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검(시험가압)","2020-09-22 13:00","2020-09-22 14:00","2020-09-22 13:00","2020-09-22 14:00","연속"]
[20,"서울","중부","용산동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #3M.Tr 1차 GIS 정밀점검(시험가압)","2020-09-17 13:00","2020-09-17 14:00","2020-09-17 13:00","2020-09-17 14:00","연속"]
[21,"서울","중부","동빙고S/S 154kV #60 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #3M.Tr 1차 GIS 정밀점검(#60BUS DS 점검 및 시험가압)","2020-09-17 14:00","2020-09-18 18:00","2020-09-17 14:00","2020-09-18 18:00","연속"]
[22,"서울","중부","용산동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #3M.Tr 1차 GIS 정밀점검(시험가압)","2020-09-18 17:00","2020-09-18 18:00","2020-09-18 17:00","2020-09-18 18:00","연속"]
[23,"서울","중부","수색S/S 154kV CB 6100","2020년 중부전력지사 170kV GIS 정밀점검(이월분)","수색S/S 154kV BUS TIE GCB 정밀점검","2020-09-10 09:00","2020-09-12 18:00","취소","취소","연속"]
[24,"서울","중부","수색중부#1 T/L","2020년 중부전력지사 170kV GIS 정밀점검(이월분)","수색S/S 154kV BUS TIE GCB 정밀점검 시험가압용","2020-09-12 17:00","2020-09-12 18:00","취소","취소","연속"]
[25,"서울","중부","양주은평#2 T/L","`20 중부P/O 변전정비회사 총액공사","T/L 보호반 교체","2020-09-21 10:00","2020-09-25 18:00","취소","취소","연속"]
[26,"서울","중부","중부아현 T/L","`20 중부P/O 변전정비회사 총액공사","T/L 보호반 교체","2020-09-07 10:00","2020-09-11 18:00","2020-09-07 10:00","2020-09-11 18:00","연속"]
[27,"서울","중부","현저서대문#2 T/L","154kV 현저S/S 옥내화 공사","모선 보호반 Goose Fail 관련 송전선로보호반 CID 파일 수정","2020-09-25 09:00","2020-09-25 18:00","2020-09-28 09:00","2020-09-28 18:00","연속"]
[28,"서울","직할","서대문세종로 T/L","20년 직할 변전협력 총액공사","서대문, 세종로S/S 서대문세종로T/L 보호반 대체","2020-09-21 10:00","2020-09-25 18:00","2020-09-21 10:00","2020-09-25 18:00","연속"]
[29,"남서울","강남","동빙고반포#2 T/L","GIS 개폐타임측정-변전협력","동빙고-반포#2T/L 개폐타임 측정","2020-09-01 12:00","2020-09-01 15:00","2020-09-03 14:00","2020-09-03 18:00","연속"]
[30,"남서울","강남","반포S/S 154kV CB 6100","GIS 개폐타임측정-변전협력","BUS TIE GIS 개폐타임 측정","2020-09-01 15:00","2020-09-01 18:00","2020-09-04 10:00","2020-09-04 14:00","연속"]
[31,"남서울","강남","동빙고반포#1 T/L","GIS 개폐타임측정-변전협력","동빙고-반포#1T/L 개폐타임 측정","2020-09-01 09:00","2020-09-01 12:00","2020-09-03 09:00","2020-09-03 14:00","연속"]
[32,"남서울","강남","신양재신사#3 T/L","GIS 개폐타임측정-변전협력","신양재-신사#3T/L GIS 개폐타임 측정","2020-09-03 14:00","2020-09-03 18:00","2020-09-01 16:00","2020-09-01 18:00","연속"]
[33,"남서울","강남","신사S/S 154kV CB 6100","GIS 개폐타임측정-변전협력","BUS TIE GIS 개폐타임 측정","2020-09-02 15:00","2020-09-02 18:00","2020-09-02 15:00","2020-09-02 18:00","연속"]
[34,"남서울","강남","신양재신사#1 T/L","GIS 개폐타임측정-변전협력","신양재-신사#1T/L GIS 개폐타임 측정","2020-09-03 09:00","2020-09-03 14:00","2020-09-01 14:00","2020-09-01 16:00","연속"]
[35,"남서울","강남","신사반포#2 T/L","GIS 개폐타임측정-변전협력","신사-반포#2T/L GIS 개폐타임 측정","2020-09-02 12:00","2020-09-02 15:00","2020-09-02 12:00","2020-09-02 15:00","연속"]
[36,"남서울","강남","신사반포#1 T/L","GIS 개폐타임측정-변전협력","신사-반포#1T/L GIS 개폐타임 측정","2020-09-02 09:00","2020-09-02 12:00","2020-09-02 09:00","2020-09-02 12:00","연속"]
[37,"남서울","동서울","강동S/S 154kV #1 BUS","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-25 14:00","2020-09-25 18:00","2020-09-25 14:00","2020-09-25 18:00","연속"]
[38,"남서울","동서울","강동S/S 154kV #2 BUS","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-23 14:00","2020-09-23 18:00","2020-09-23 14:00","2020-09-23 18:00","연속"]
[39,"남서울","동서울","동남S/S 154kV CB 6100","모선보호반 교체공사","모선보호반 교체공사","2020-09-14 09:00","2020-09-18 18:00","취소","취소","연속"]
[40,"남서울","동서울","동서울신장#1 T/L","154kV 동서울-강동T/L 등 5개T/L 지중화(이설)공사","154KV 동서울-신장T/L 가철탑 연선 및 긴선","2020-09-12 09:00","2020-09-20 18:00","취소","취소","연속"]
[41,"남서울","동서울","동서울신장#2 T/L","154kV 동서울-강동T/L 등 5개T/L 지중화(이설)공사","154KV 동서울-신장T/L 가철탑 연선 및 긴선","2020-09-21 09:00","2020-09-26 18:00","취소","취소","연속"]
[42,"남서울","동서울","논현선릉#1 T/L","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-18 14:00","2020-09-18 18:00","2020-09-18 14:00","2020-09-18 18:00","연속"]
[43,"남서울","동서울","논현선릉#1 T/L","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-11 14:00","2020-09-11 18:00","2020-09-11 14:00","2020-09-11 18:00","연속"]
[44,"남서울","동서울","논현선릉#1 T/L","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-16 14:00","2020-09-16 18:00","2020-09-16 14:00","2020-09-16 18:00","연속"]
[45,"남서울","동서울","논현선릉#1 T/L","170kV GIS 정밀점검 무부하 가압용","170kV GIS 정밀점검 무부하 가압용","2020-09-09 14:00","2020-09-09 18:00","2020-09-09 14:00","2020-09-09 18:00","연속"]
[46,"남서울","동서울","천호S/S 154kV CB 6100","모선보호반 교체공사","모선보호반 교체공사","2020-09-21 09:00","2020-09-25 18:00","2020-09-21 09:00","2020-09-25 18:00","연속"]
[47,"남서울","영등포","가양등촌#1 T/L","154kV 가양S/S 인출전력구 케이블 선종교체공사","가양S/S 인출전력구 케이블 선종교체공사 구간 : 가양S/S EBG ~ J/B#1","2020-09-01 09:00","2020-10-26 18:00","취소","취소","연속"]
[48,"남서울","영등포","대방신길#1 T/L","154kV 대방인출전력구 OF케이블 선종교체공사","공사개요 대방 인출전력구 내 154kV 대방-신길#1T/L 선종교체 공사 - 구간 : 대방S/S~J/B#38 - 교체전 : OF 1200, 교체후 : XLPE 1200","2020-09-01 09:00","2020-10-08 18:00","2020-09-07 09:00","2020-10-16 18:00","연속"]
[49,"남서울","영등포","신정S/S 154kV #60 BUS","154kV 신정S/S #3M.Tr용 GIS 설치공사","-154kV GIS 설치×1식 -23kV GIS 설치×1식","2020-09-21 09:00","2020-09-23 18:00","2020-09-21 09:00","2020-09-23 18:00","연속"]
[50,"남서울","영등포","신정S/S 154kV #65 BUS","154kV 신정S/S #3M.Tr용 GIS 설치공사","-154kV GIS 설치×1식 -23kV GIS 설치×1식","2020-09-24 09:00","2020-09-26 18:00","2020-09-24 09:00","2020-09-26 18:00","연속"]
[51,"남서울","영등포","신정목동#1 T/L","154kV 신정S/S #3M.Tr용 GIS 설치공사","-170kV GIS 설치× 1식 -모선 GIB 연결시 인근 선로 휴전 필요(DS부 활선구간) -병행작업 : 신정목동#1T/L 보호반 대체(9/24-9/25) -60BUS 24시간 무부하가압:6/22 18:00 - 6/23 18:00 -65BUS 24시간 무부하가압:6/25 18:00 - 6/26 18:00","2020-09-21 09:00","2020-09-26 18:00","2020-09-21 09:00","2020-09-26 18:00","연속"]
[52,"남서울","영등포","신정목동#2 T/L","154kV 신정S/S #3M.Tr용 GIS 설치공사","-170kV GIS 설치× 1식 -모선 GIB 연결시 인근 선로 휴전 필요(DS부 활선구간) -병행작업 : 신정목동#2T/L 보호반 대체(9/21-9/23)","2020-09-21 09:00","2020-09-26 18:00","2020-09-21 09:00","2020-09-26 18:00","연속"]
[53,"남서울","영등포","천왕오류#1 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험(오류변전소측)","2020-09-05 09:00","2020-09-06 18:00","2020-09-30 09:00","2020-10-03 18:00","연속"]
[54,"남서울","영등포","천왕오류#2 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험(오류변전소측)","2020-09-26 09:00","2020-09-27 18:00","2020-09-26 09:00","2020-09-27 18:00","연속"]
[55,"남서울","영등포","천왕오류#2 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험(천왕변전소측)","2020-09-12 09:00","2020-09-13 18:00","취소","취소","연속"]
[56,"남서울","영등포","천왕오류#1 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험(천왕변전소측)","2020-09-19 09:00","2020-09-20 18:00","취소","취소","연속"]
[57,"남서울","영등포","화곡마곡#1 T/L","화곡S/S 154kV 송전선로 보호반 43PDA 교체","- 보호반 43PDA 접점 불량발생으로 교체","2020-09-24 09:00","2020-09-24 18:00","취소","취소","연속"]
[58,"남서울","직할","신길S/S 154kV CB 6100","23kV GIS 증설공사 관련 계통 통합","신길S/S 23kV GIS 증설 관련 계통 통합","2020-09-01 09:00","2020-09-04 18:00","2020-09-01 09:00","2020-09-04 18:00","연속"]
[59,"인천","김포","경서양촌#2 T/L","154kV 경서-양촌T/L 지중화 관련 가이설공사","○ 한들지구 : 4기신설,3기철거 ○ 검단3구역 : 5기신설,3기철거 ○ 대포산업단지 : 4기신설, 2기철거","2020-09-11 07:00","2020-09-13 18:00","2020-09-11 07:00","2020-09-13 18:00","연속"]
[60,"인천","김포","경서양촌#1 T/L","154kV 경서-양촌T/L 지중화 관련 가이설공사","○ 한들지구 : 4기신설,3기철거 ○ 검단3구역 : 5기신설,3기철거 ○ 대포산업단지 : 4기신설, 2기철거","2020-09-14 07:00","2020-09-20 18:00","2020-09-14 07:00","2020-09-20 18:00","연속"]
[61,"인천","김포","경서양촌#2 T/L","154kV 경서-양촌T/L 지중화 관련 가이설공사","○ 한들지구 : 4기신설,3기철거 ○ 검단3구역 : 5기신설,3기철거 ○ 대포산업단지 : 4기신설, 2기철거","2020-09-21 07:00","2020-09-26 18:00","2020-09-21 07:00","2020-09-26 18:00","연속"]
[62,"인천","김포","신김포양곡#1 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-22 10:00","2020-09-22 17:00","취소","취소","연속"]
[63,"인천","김포","신김포양곡#2 T/L","양곡S/S 154kV 신김포-양곡#2T/L GIS 조작시험","양곡S/S 154kV 신김포-양곡#2T/L GIS 조작시험(전자변 교체 병행)","2020-09-25 10:00","2020-09-25 18:00","취소","취소","연속"]
[64,"인천","김포","왕길양촌#1 T/L","김포전력지사-양촌S/S 광케이블 시설공사","김포전력지사-양촌S/S 광케이블 시설(OPGW 1.49km, OFC 2.8km)","2020-09-28 09:00","2020-10-02 18:00","취소","취소","연속"]
[65,"인천","김포","왕길양촌#2 T/L","154kV 왕길-양촌#2T/L 초기점검","154kV 왕길-양촌#2T/L 초기점검","2020-09-07 09:30","2020-09-08 18:00","2020-09-07 09:30","2020-09-08 18:00","연속"]
[66,"인천","부평","남인천S/S 154kV CB 6100","남인천S/S 170kV 6100 BUS-TIE GIS 조작시험","남인천S/S 170kV 6100 BUS-TIE GIS 조작시험","2020-09-24 09:00","2020-09-24 18:00","2020-09-18 09:00","2020-09-18 18:00","연속"]
[67,"인천","부평","관교만수#2 T/L","154kV 관교-만수#2T/L PT 및 채유밸브 보강","154kV 관교-만수#2T/L PT 및 채유밸브 보강","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]
[68,"인천","부평","만수S/S 154kV CB 6200","만수S/S 170kV 6200 BUS-TIE GIS 초기점검","만수S/S 170kV 6200 BUS-TIE GIS 초기점검","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[69,"인천","부평","부흥부개#1 T/L","부개S/S 170kV 부흥부개#1 T/L GIS 보통점검","부개S/S 170kV 부흥부개#1 T/L GIS 보통점검","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[70,"인천","부평","부흥부개#2 T/L","부개S/S 170kV 부흥부개#2 T/L GIS 보통점검","부개S/S 170kV 부흥부개#2 T/L GIS 보통점검","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[71,"인천","부평","서인천C/C 154kV CB 6333","서인천복합S/Y 170kV #3G.Tr(6333) GIS 조작시험 공사","서인천복합S/Y 170kV #3G.Tr(6333) GIS 조작시험 공사","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[72,"인천","부평","신가좌인천#2 T/L","신가좌S/S 신가좌-인천#2T/L 보호반 교체공사","신가좌S/S 신가좌-인천#2T/L 보호반 교체공사 - 병행작업 : 인천S/S 신가좌-인천#2T/L 보호반 교체공사","2020-09-14 09:00","2020-09-18 18:00","2020-09-14 09:00","2020-09-18 18:00","연속"]
[73,"인천","부평","신경서영종 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-21 10:00","2020-09-21 17:00","2020-09-21 10:00","2020-09-21 17:00","연속"]
[74,"인천","부평","영종S/S 154kV #1 Sh.R CB","영종S/S 170kV #1 Sh.R 1차 GIS 하자점검","영종S/S 170kV #1 Sh.R 1차 GIS 하자점검","2020-09-23 09:00","2020-09-23 18:00","취소","취소","연속"]
[75,"인천","부평","인천남인천#2 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-23 14:00","2020-09-23 17:00","취소","취소","연속"]
[76,"인천","부평","인천남인천#1 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-23 10:00","2020-09-23 14:00","취소","취소","연속"]
[77,"인천","부평","남인천학익#1 T/L","학익S/S 154kV #1M.Tr 및 1차 GIS 무부하가압","학익S/S 154kV #1M.Tr 및 1차 GIS 무부하가압","2020-09-25 13:00","2020-09-25 18:00","2020-09-18 13:00","2020-09-18 18:00","연속"]
[78,"인천","시흥","북송도연수#1 T/L","154kV 북송도S/S #4M.Tr 증설관련 GIS 설치공사","154kV 북송도S/S M.Tr 증설공사(#60BUS 무부하가압) -170kV GIS 1CCT 설치 -25.8kV GIS 1CCT 설치 -기타부대공사","2020-09-18 18:00","2020-09-19 18:00","2020-09-18 18:00","2020-09-19 18:00","연속"]
[79,"인천","시흥","북송도연수#1 T/L","154kV 북송도S/S #4M.Tr 증설관련 GIS 설치공사","154kV 북송도S/S M.Tr 증설공사(#65BUS 무부하가압) -170kV GIS 1CCT 설치 -25.8kV GIS 1CCT 설치 -기타부대공사","2020-09-24 18:00","2020-09-25 18:00","2020-09-24 18:00","2020-09-25 18:00","연속"]
[80,"인천","시흥","북시화서시화#2 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차) - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-01 07:30","2020-09-28 18:00","2020-09-01 07:30","2020-09-28 18:00","연속"]
[81,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_#2BUS 무부하가압(시험가압))15H - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-03 17:00","2020-09-04 07:30","2020-09-03 17:00","2020-09-04 07:30","연속"]
[82,"인천","시흥","서시화S/S 154kV #1 BUS","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차) - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-04 07:30","2020-09-15 07:30","2020-09-04 07:30","2020-09-15 07:30","연속"]
[83,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_#1BUS 무부하가압(시험가압)) - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-13 18:00","2020-09-15 07:30","2020-09-13 18:00","2020-09-15 07:30","연속"]
[84,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_최종 무부하가압 - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-26 18:00","2020-09-28 07:30","2020-09-26 18:00","2020-09-28 13:00","연속"]
[85,"인천","시흥","서시화S/S 154kV #2 BUS","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차) - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-15 07:30","2020-09-28 07:30","2020-09-15 07:30","2020-09-28 10:00","연속"]
[86,"인천","시흥","서서울#2소래 T/L","154kV서서울2소래T/L 추락방지시설 설치공사","154kV서서울2소래T/L 추락방지시설 설치공사(No.70)","2020-09-22 08:00","2020-09-22 12:00","2020-09-22 08:00","2020-09-22 12:00","연속"]
[87,"인천","시흥","서안양소래 T/L","154kV서안양소래T/L 추락방지시설 설치공사","154kV서안양소래T/L 추락방지시설 설치공사(No.70)","2020-09-22 12:00","2020-09-22 16:00","2020-09-22 12:00","2020-09-22 16:00","연속"]
[88,"인천","시흥","신시흥도림#1 T/L","154kV 신시흥-남동T/L 지장송전선로 이설공사","○ 구간 : No.16~18 ○ 전력선 : ACSR/AW 410㎟ × 2B × 4C ○ 작업내용 : 임시철탑 1기 설치(No.17)","2020-09-25 13:00","2020-09-29 18:00","2020-09-25 13:00","2020-09-29 18:00","연속"]
[89,"인천","시흥","신시흥남동#2 T/L","154kV 신시흥-남동T/L 지장송전선로 이설공사","○ 구간 : No.16~18 ○ 전력선 : ACSR/AW 410㎟ × 2B × 4C ○ 작업내용 : 임시철탑 1기 설치(No.17)","2020-09-21 07:00","2020-09-25 13:00","2020-09-21 07:00","2020-09-25 13:00","연속"]
[90,"인천","시흥","신시흥도림#2 T/L","154kV 신시흥-남동T/L 지장송전선로 이설공사","○ 구간 : No.16~18 ○ 전력선 : ACSR/AW 410㎟ × 2B × 4C ○ 작업내용 : 임시철탑 1기 설치(No.17)","2020-09-21 07:00","2020-09-25 13:00","2020-09-21 07:00","2020-09-25 13:00","연속"]
[91,"인천","시흥","신시흥남동#1 T/L","154kV 신시흥-남동T/L 지장송전선로 이설공사","○ 구간 : No.16~18 ○ 전력선 : ACSR/AW 410㎟ × 2B × 4C ○ 작업내용 : 임시철탑 1기 설치(No.17)","2020-09-25 13:00","2020-09-29 18:00","2020-09-25 13:00","2020-09-29 18:00","연속"]
[92,"인천","시흥","신시흥시화#2 T/L","154kV 신시흥-시화T/L 추락방지시설 설치공사","154kV 신시흥-시화T/L 추락방지시설 설치공사(No.12,13)","2020-09-21 13:00","2020-09-21 18:00","2020-09-21 13:00","2020-09-21 18:00","연속"]
[93,"인천","시흥","신시흥시화#1 T/L","154kV 신시흥-시화T/L 추락방지시설 설치공사","154kV 신시흥-시화T/L 추락방지시설 설치공사(No.12,13)","2020-09-21 08:00","2020-09-21 13:00","2020-09-21 08:00","2020-09-21 13:00","연속"]
[94,"인천","직할","부천도당#1 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-28 10:00","2020-09-28 14:00","취소","취소","연속"]
[95,"인천","직할","부천도당#2 T/L","선도제 154kV 송전선로보호계전기 성능개선","87,21계전기 펌웨어 업데이트 시행","2020-09-28 14:00","2020-09-28 17:00","취소","취소","연속"]
[96,"인천","직할","인천CC북인천#2 T/L","북인천S/S 인천CC-북인천#2T/L 보호반 대체공사","북인천S/S 인천CC-북인천#2T/L 보호반 대체공사","2020-09-21 09:30","2020-09-25 18:00","2020-09-21 09:30","2020-09-25 18:00","연속"]
[97,"인천","시흥","북시화서시화#1 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_#2BUS 무부하가압(시험가압))15H - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-03 17:00","2020-09-04 07:30","취소","취소","연속"]
[98,"인천","시흥","북시화서시화#1 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_#1BUS 무부하가압(시험가압)) - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-13 18:00","2020-09-15 07:30","취소","취소","연속"]
[99,"인천","시흥","북시화서시화#1 T/L","서시화S/S 170kV GIS 대체공사","서시화S/S 170kV GIS 대체공사(1차)_최종 무부하가압 - 북시화서시화#2T/L, #2M.Tr 1차 GIS 대체","2020-09-26 18:00","2020-09-28 07:30","취소","취소","연속"]
[100,"경기북부","고양","고양S/S 154kV #65 BUS","154kV 고양S/S #3M.Tr 증설 공사","- 주변압기 x 1Bank 설치 - 170kV GIS x 1CCT 설치 - 23kV SIS x 9CCT 설치 - 기타 부대공사 1식","2020-09-26 00:00","2020-09-26 18:00","2020-09-26 00:00","2020-09-26 18:00","연속"]
[101,"경기북부","고양","고양S/S 154kV #60 BUS","154kV 고양S/S #3M.Tr 증설 공사","- 주변압기 x 1Bank 설치 - 170kV GIS x 1CCT 설치 - 23kV SIS x 9CCT 설치 - 기타 부대공사 1식","2020-09-25 18:00","2020-09-26 00:00","2020-09-25 18:00","2020-09-26 00:00","연속"]
[102,"경기북부","고양","양주고양#1 T/L","154kV 고양S/S #3M.Tr 증설 공사","- 주변압기 x 1Bank 설치 - 170kV GIS x 1CCT 설치 - 23kV SIS x 9CCT 설치 - 기타 부대공사 1식","2020-09-25 18:00","2020-09-26 18:00","2020-09-25 18:00","2020-09-26 18:00","연속"]
[103,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(#1BUS 시험가압)","170kV GIS #1BUS 시험가압","2020-09-12 17:00","2020-09-14 10:00","2020-09-12 17:00","2020-09-14 10:00","연속"]
[104,"경기북부","고양","신덕은금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#2T/L 170kV GIS 월붓싱 철거시 안전이격확보","2020-09-05 09:00","2020-09-05 17:00","2020-09-05 09:00","2020-09-05 17:00","연속"]
[105,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(#2BUS 시험가압)","170kV GIS #2BUS 시험가압","2020-09-03 17:00","2020-09-04 10:00","2020-09-03 17:00","2020-09-04 10:00","연속"]
[106,"경기북부","고양","신덕은금촌#2 T/L","2020년 금촌S/S 170kV GIS 교체공사","금촌S/S 신덕은-금촌#2T/L GIS 교체공사","2020-09-01 09:00","2020-09-28 15:00","2020-09-01 09:00","2020-09-28 15:00","연속"]
[107,"경기북부","고양","신덕은금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#2T/L 170kV GIS 월붓싱 설치시 안전이격확보","2020-09-19 09:00","2020-09-19 17:00","2020-09-19 09:00","2020-09-19 17:00","연속"]
[108,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(교체 GIS 시험가압)","170kV GIS 교체분 시험가압","2020-09-26 17:00","2020-09-28 15:00","2020-09-26 17:00","2020-09-28 15:00","연속"]
[109,"경기북부","고양","남면백석#2 T/L","2020년도 가공송전 순시점검 위탁공사","초기점검","2020-09-18 08:00","2020-09-18 18:00","2020-09-18 08:00","2020-09-18 18:00","매일"]
[110,"경기북부","고양","남면백석#1 T/L","2020년도 가공송전 순시점검 위탁공사","초기점검","2020-09-17 08:00","2020-09-17 18:00","2020-09-17 08:00","2020-09-17 18:00","매일"]
[111,"경기북부","고양","원흥수색#1 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-29 07:00","2020-09-29 18:00","2020-09-27 13:00","2020-09-27 18:00","연속"]
[112,"경기북부","고양","원흥상암 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-28 07:00","2020-09-28 18:00","2020-09-27 09:00","2020-09-27 13:00","연속"]
[113,"경기북부","고양","월롱금촌#2 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-28 07:00","2020-09-28 18:00","2020-09-26 07:00","2020-09-26 13:00","연속"]
[114,"경기북부","고양","월롱금촌#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 정밀점검(안전이격거리 확보휴전)","2020-09-29 08:00","2020-09-29 18:00","2020-09-29 08:00","2020-09-29 18:00","매일"]
[115,"경기북부","고양","지도능곡#1 T/L","154kV 지도-능곡#1T/L OF케이블 선종교체공사","154kV 지도-능곡#1T/L EBG ~ S/J구간 OF → XLPE 케이블 선종교체공사","2020-09-01 09:00","2020-10-30 18:00","취소","취소","연속"]
[116,"경기북부","고양","일산호수#1 T/L","20~21년 고양전력지사 변전정비회사 총액공사","송전선로 보호배전반 교체공사","2020-09-16 09:00","2020-09-18 18:00","2020-09-16 09:00","2020-09-18 18:00","연속"]
[117,"경기북부","구리","덕소마석#1 T/L","관형지지물 작업자 추락방지시설 설치","154kV 덕소-마석#1T/L No.45,46관형지지물 작업자 추락방지시설 설치","2020-09-28 08:00","2020-09-28 18:00","2020-09-28 08:00","2020-09-28 18:00","연속"]
[118,"경기북부","구리","덕소마석#2 T/L","관형지지물 작업자 추락방지시설 설치","154kV 덕소-마석#2T/L No.45,46관형지지물 작업자 추락방지시설 설치","2020-09-29 08:00","2020-09-29 18:00","2020-09-29 08:00","2020-09-29 18:00","연속"]
[119,"경기북부","구리","미금화양 T/L","154kV 미금-화양T/L 정밀점검","- No.3등 철탑21기 정밀점검","2020-09-07 09:00","2020-09-10 18:00","2020-09-07 09:00","2020-09-10 18:00","연속"]
[120,"경기북부","구리","미금광장 T/L","154kV 미금-광장T/L 정밀점검","- No.3등 철탑21기 정밀점검","2020-09-14 09:00","2020-09-16 18:00","2020-09-14 09:00","2020-09-16 18:00","연속"]
[121,"경기북부","구리","미금덕소#2 T/L","미금S/S 감시제어설비 교체공사","- 노후 모자익반 및 현장조작반간 제어케이블 교체 (아날로그 → 디지털SA)","2020-09-21 09:00","2020-09-25 18:00","2020-09-21 09:00","2020-09-25 18:00","연속"]
[122,"경기북부","구리","동서울서종#2 T/L","154kV 동서울-서종#2T/L 불량애자교체공사","No.39호 하단부하측 불량애자교체공사","2020-09-11 13:00","2020-09-11 18:00","2020-09-17 13:00","2020-09-17 18:00","연속"]
[123,"경기북부","구리","동서울서종#1 T/L","154kV 동서울-서종#1T/L 불량애자교체공사","No.38호 상단전원측 불량애자교체공사","2020-09-11 07:00","2020-09-11 13:00","2020-09-17 07:00","2020-09-17 13:00","연속"]
[124,"경기북부","구리","서종청평PP#2 T/L","154kV 서종-청평PPT/L 전선접속개소 전선교체공사","154kV 서종-청평PP#2T/L No.58~60, 61~63 전선접속개소 전선교체공사","2020-09-21 07:00","2020-09-26 18:00","2020-09-21 07:00","2020-09-26 18:00","연속"]
[125,"경기북부","구리","서종청평PP#1 T/L","154kV 서종-청평PPT/L 전선접속개소 전선교체공사","154kV 서종-청평PP#1T/L No.58~60, 61~63 전선접속개소 전선교체공사","2020-09-14 07:00","2020-09-19 18:00","2020-09-16 07:00","2020-09-20 18:00","연속"]
[126,"경기북부","구리","신포천백학#2 T/L","2020년 가공송전선로 순시점검 위탁공사","아킹혼 철거","2020-09-17 08:00","2020-09-21 18:00","2020-09-17 08:00","2020-09-21 18:00","연속"]
[127,"경기북부","구리","신포천동두천#2 T/L","2020년 가공송전선로 순시점검 위탁공사","아킹혼 철거","2020-09-22 09:00","2020-09-25 18:00","2020-09-22 09:00","2020-09-25 18:00","연속"]
[128,"경기북부","구리","신포천포천#1 T/L","2020년 가공송전선로 순시점검 위탁공사","아킹혼 철거","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]
[129,"경기북부","구리","신포천덕계#2 T/L","20~21년 경기북부 직할 가공송전정비회사 총액공사","ㅇ 항공장애표시구 설치 - 대상 : No.7~8","2020-09-24 14:00","2020-09-24 18:00","2020-09-24 14:00","2020-09-24 18:00","연속"]
[130,"경기북부","구리","신포천덕계#1 T/L","관내 OPGW 항공장애표시구 설치공사(2020)","- 154kV 신포천덕계 #1T/L OPGW 7호~8호 구간 항공장애표시구 4개 설치","2020-09-29 08:00","2020-09-29 18:00","2020-09-29 08:00","2020-09-29 18:00","연속"]
[131,"경기북부","구리","포천포천열병합 T/L CB","포천S/S 포천열병합T/L 인출 접속부 과열개소 보수","포천열병합T/L 인출 접속부(EBA) 과열개소 점검 및 GCB 보통점검","2020-09-03 09:00","2020-09-04 18:00","2020-09-03 09:00","2020-09-04 18:00","연속"]
[132,"경기북부","구리","포천S/S 154kV #1 BUS","포천S/S 154kV BUSTIE 이설공사","포천S/S 154kV BUSTIE 이설공사 - 9.1(화) : 154kV #1Sh.C GIS - #60BUS 간 인하선 철거 - 9.14(월)~9.18(금) : #60BUS LA, CVT 기초공사","2020-09-21 09:00","2020-10-02 18:00","2020-09-21 09:00","2020-10-02 18:00","매일"]
[133,"경기북부","직할","백석덕계#2 T/L","관내 OPGW 항공장애표시구 설치공사(2020)","- 154kV 백석덕계 #2T/L OPGW 21호~22호 구간 항공장애표시구 4개 설치","2020-09-28 08:00","2020-09-28 18:00","2020-09-28 08:00","2020-09-28 18:00","연속"]
[134,"경기북부","직할","백석덕계#1 T/L","20~21년 경기북부 직할 가공송전정비회사 총액공사","ㅇ 항공장애표시구 설치 - 대상 : No.21~22","2020-09-24 08:00","2020-09-24 14:00","2020-09-24 08:00","2020-09-24 14:00","연속"]
[135,"경기북부","직할","신의정부내촌#2 T/L","20~21년 경기북부본부 직할 가공송전정비회사 총액공사","ㅇ 345kV 신가평-신의정부#2T/L 항공장애표시구 설치공사 - 병가선로","2020-09-25 14:00","2020-09-25 18:00","2020-09-25 14:00","2020-09-25 18:00","연속"]
[136,"경기북부","직할","양주고양#2 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-고양#2T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-09-01 08:00","2020-09-25 18:00","2020-09-01 08:00","2020-09-25 18:00","연속"]
[137,"경기북부","직할","양주금촌#1 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-금촌#1 T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-09-01 08:00","2020-09-25 18:00","2020-09-01 08:00","2020-09-25 18:00","연속"]
[138,"경기북부","직할","양주S/S 154kV #62 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[139,"경기북부","직할","양주S/S 154kV #61 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[140,"경기북부","직할","양주S/S 154kV #60 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[141,"경기북부","직할","양주S/S 154kV #67 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[142,"경기북부","직할","양주S/S 154kV #60 BUS","20~21년 변전정비회사 총액공사","345kV #1M.Tr 6161DS 과열개소 보수작업","2020-09-03 09:00","2020-09-03 18:00","2020-09-03 09:00","2020-09-03 18:00","연속"]
[143,"경기북부","직할","양주쌍문#1 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-28 07:00","2020-09-28 18:00","2020-09-28 07:00","2020-09-28 18:00","연속"]
[144,"경기북부","직할","양주쌍문#2 T/L","20-21년도 가공송전 정비회사 총액공사","ㅇ 불량애자교체","2020-09-29 07:00","2020-09-29 18:00","2020-09-29 07:00","2020-09-29 18:00","연속"]
[145,"경기북부","직할","옥정동두천#2 T/L","2020년 가공송전선로 순시점검 위탁공사","전선접속개소 편심진단","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[146,"경기북부","직할","도봉진접 T/L","154kV 도봉-진접T/L 송전선로 피뢰기 설치공사","154kV 도봉-진접T/L No.10 등 철탑 20기 피뢰기 설치공사","2020-09-16 07:00","2020-09-18 18:00","2020-09-14 07:00","2020-09-16 18:00","연속"]
[147,"경기","군포","화성마도 T/L","마도S/S 화성-마도T/L GIS 하자점검","마도S/S 화성-마도T/L GIS 하자점검","2020-09-26 09:00","2020-09-26 18:00","2020-09-26 09:00","2020-09-26 18:00","연속"]
[148,"경기","군포","반월시화#1 T/L","반월S/S 154kV GIS 패킹 불량 관련 하자 조치, GIS 하자점검","반월S/S 154kV GIS 패킹 불량 관련 하자 조치, GIS 하자점검","2020-09-28 10:00","2020-09-28 14:00","2020-09-28 10:00","2020-09-28 14:00","연속"]
[149,"경기","군포","서서울#2일동#1 T/L","2020-2021년도 송전정비회사 총액공사","- 애자장치 교체 :7기","2020-09-25 08:00","2020-09-26 18:00","2020-09-25 08:00","2020-09-26 18:00","연속"]
[150,"경기","군포","서서울#2일동#2 T/L","2020-2021년도 송전정비회사 총액공사","- 송전용 피뢰기 설치 : 19기, 애자장치 교체 :7기","2020-09-21 08:00","2020-09-24 18:00","2020-09-21 08:00","2020-09-24 18:00","연속"]
[151,"경기","군포","서서울율전#2 T/L","서서울#1S/S 서서울-율전#2T/L GIS 하자점검","서서울#1S/S 서서울-율전#2T/L GIS 하자점검","2020-09-28 14:00","2020-09-28 18:00","2020-09-28 14:00","2020-09-28 18:00","연속"]
[152,"경기","군포","서서울율전#1 T/L","서서울#1S/S 서서울-율전#1T/L GIS 하자점검","서서울#1S/S 서서울-율전#1T/L GIS 하자점검","2020-09-28 09:00","2020-09-28 14:00","2020-09-28 09:00","2020-09-28 14:00","연속"]
[153,"경기","군포","시화동시화#1 T/L","시화S/S 시화-동시화#1T/L GIS 전자변교체, 히터설치","시화S/S 시화-동시화#1T/L GIS 전자변교체, 히터설치","2020-09-28 09:00","2020-09-28 14:00","2020-09-28 09:00","2020-09-28 14:00","연속"]
[154,"경기","군포","시화동시화#2 T/L","시화S/S 시화-동시화#2T/L GIS 보통, 전자변교체, 히터교체","시화S/S 시화-동시화#2T/L GIS 보통, 전자변교체, 히터교체","2020-09-28 14:00","2020-09-28 18:00","2020-09-28 14:00","2020-09-28 18:00","연속"]
[155,"경기","동부","곤지암이천#1 T/L","20년 동부 변전정비회사 총액공사","지암:곤지암-이천#1T/L(보통) LA(보통), 이천:곤지암-이천#1T/L(보통), 43L/R 회로보완 확인 및 Remote 회로분리 시행, LA(초기)-","2020-09-26 09:30","2020-09-26 18:00","2020-09-26 09:30","2020-09-26 18:00","연속"]
[156,"경기","동부","모현용인#1 T/L","154kV 모현S/S SW 증설공사","154kV 모현S/S SW 증설공사 - 무부하가압 선로","2020-09-28 09:00","2020-09-29 18:00","2020-09-28 09:00","2020-09-29 18:00","연속"]
[157,"경기","동부","분당C/C 154kV CB 6100","20년 동부 변전정비회사 총액공사","분당:6100 GIS(보통),6200 GIS(조작)43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-09-21 09:30","2020-09-21 14:00","2020-09-21 09:30","2020-09-21 14:00","연속"]
[158,"경기","동부","오천율현#2 T/L","오천S/S #1M.Tr 설치공사","오천S/S 154kV #1M.Tr 증설 관련 최초가압 및 무부하가압","2020-09-23 09:00","2020-09-24 18:00","2020-09-23 09:00","2020-09-24 18:00","연속"]
[159,"경기","동부","곤지암초월#1 T/L","154kV초월-성현T/L 불량애자 교체공사","154kV초월-성현T/L 불량애자 교체공사 안전이격확보","2020-09-21 09:00","2020-09-23 18:00","2020-09-21 09:00","2020-09-23 18:00","매일"]
[160,"경기","동부","초월성현#2 T/L","154kV초월-성현T/L 불량애자 교체공사","154kV초월-성현T/L 불량애자 교체공사","2020-09-24 09:00","2020-09-26 18:00","2020-09-24 09:00","2020-09-26 18:00","매일"]
[161,"경기","동부","곤지암초월#2 T/L","154kV초월-성현T/L 불량애자 교체공사","154kV초월-성현T/L 불량애자 교체공사 안전이격확보","2020-09-24 09:00","2020-09-26 18:00","2020-09-24 09:00","2020-09-26 18:00","매일"]
[162,"경기","동부","초월성현#1 T/L","154kV초월-성현T/L 불량애자 교체공사","154kV초월-성현T/L 불량애자 교체공사","2020-09-21 09:00","2020-09-23 18:00","2020-09-21 09:00","2020-09-23 18:00","매일"]
[163,"경기","성남","진위동탄#2 T/L","20년 성남전력 변전정비회사 총액공사","세니온성능개선","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[164,"경기","성남","진위동탄#1 T/L","20년 성남전력 변전정비회사 총액공사","세니온성능개선","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[165,"경기","성남","북동탄동탄2열병합#1 T/L","송전선로 보호 IED(21) 성능개선","송전선로 보호 IED(21) 성능개선","2020-09-21 09:00","2020-09-21 14:00","2020-09-21 09:00","2020-09-21 14:00","연속"]
[166,"경기","성남","북동탄동탄2열병합#2 T/L","송전선로 보호 IED(21) 성능개선","송전선로 보호 IED(21) 성능개선","2020-09-21 14:00","2020-09-21 18:00","2020-09-21 14:00","2020-09-21 18:00","연속"]
[167,"경기","직할","조암구문천#1 T/L","20년 직할 변전정비회사 총액공사","구문천S/S 조암-구문천 #1T/L GIS 보통점검","2020-09-29 09:00","2020-09-29 18:00","2020-09-29 09:00","2020-09-29 18:00","연속"]
[168,"경기","직할","조암구문천#2 T/L","20년 직할 변전정비회사 총액공사","구문천S/S 조암-구문천 #2T/L GIS 보통점검","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[169,"경기","직할","남수원발안#1 T/L","남수원S/S SA혼용시스템 설치","남수원S/S SA혼용시스템 설치 1식","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[170,"경기","직할","봉담남수원#2 T/L","봉담-송산간 3공구 도로개설 관련 지장이설","관형지지물 3기, 산형강 1기 추락방지장치 설치 및 환경도장","2020-09-18 07:00","2020-09-19 18:00","2020-09-18 07:00","2020-09-19 18:00","연속"]
[171,"경기","직할","봉담남수원#1 T/L","봉담-송산간 3공구 도로개설 관련 지장이설","관형지지물 3기, 산형강 1기 추락방지장치 설치 및 환경도장","2020-09-18 07:00","2020-09-19 18:00","2020-09-18 07:00","2020-09-19 18:00","연속"]
[172,"경기","직할","남수원발안#2 T/L","남수원S/S SA혼용시스템 설치","남수원S/S SA혼용시스템 설치 1식","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[173,"경기","직할","서서울#2봉담#2 T/L","세니온 계전기 업데이트 관련 휴전신청","봉담S/S 서서울2봉담#2 T/L 세니온 계전기 업데이트","2020-09-21 14:00","2020-09-21 18:00","2020-09-21 14:00","2020-09-21 18:00","연속"]
[174,"경기","직할","서서울#2봉담#1 T/L","세니온 계전기 업데이트 관련 휴전신청","봉담S/S 서서울2봉담#1 T/L 세니온 계전기 업데이트","2020-09-21 09:00","2020-09-21 14:00","2020-09-21 09:00","2020-09-21 14:00","연속"]
[175,"경기","직할","화성수촌#2 T/L","154kV 수촌S/S #1M.Tr 증설공사","수촌S/S 154kV #60BUS 무부하가압","2020-09-17 17:00","2020-09-18 17:00","2020-09-17 17:00","2020-09-18 17:00","연속"]
[176,"경기","직할","화성수촌#2 T/L","154kV 수촌S/S #1M.Tr 증설공사","수촌S/S 154kV #65BUS 무부하가압","2020-09-24 17:00","2020-09-25 17:00","2020-09-24 17:00","2020-09-25 17:00","연속"]
[177,"경기","직할","안양평촌#2 T/L","20년 직할 변전정비회사 총액공사","평촌S/S 안양-평촌 #2T/L 보통, 안양-평촌#2T/L LA 보통, GIS 전자변 교체","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[178,"경기","직할","평촌안양2CC#2 T/L","20년 직할 변전정비회사 총액공사","평촌S/S 평촌-안양열병합 #2T/L GIS 하자, LA 보통 안양복합S/Y 평촌-안양열병합 #2T/L GIS 하자, LA 하자","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[179,"경기","직할","평촌안양2CC#1 T/L","20년 직할 변전정비회사 총액공사","평촌S/S 평촌-안양열병합 #1T/L GIS 하자, LA 보통 안양복합S/Y 평촌-안양열병합 #1T/L GIS 하자, LA 하자","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[180,"경기","직할","평촌안양2CC#3 T/L","20년 직할 변전정비회사 총액공사","평촌S/S 평촌-안양열병합 #3T/L GIS 하자, LA 보통 안양복합S/Y 평촌-안양열병합 #3T/L GIS 하자, LA 하자","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[181,"경기","직할","안양평촌#1 T/L","20년 직할 변전정비회사 총액공사","평촌S/S 안양-평촌 #1T/L 조작","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[182,"경기","평택","서안성안성#1 T/L","서안성S/S 154kV 서안성-안성#1T/L GIS 누기보수","서안성S/S 154kV 서안성-안성#1T/L GIS 누기보수","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[183,"경기","평택","서운삼죽 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼설치(25기)","2020-09-14 08:00","2020-09-17 18:00","2020-09-14 08:00","2020-09-17 18:00","매일"]
[184,"경기","평택","서운삼죽 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","현수애자 절연성능진단 (중각도 철탑 2기)","2020-09-01 09:00","2020-09-02 18:00","2020-09-01 09:00","2020-09-02 18:00","매일"]
[185,"경기","평택","오산향남#1 T/L","화성정남 전력구 운영시스템 설치공사","CCTV 및 PD진단 단자집합반 설치공사","2020-09-22 09:00","2020-09-25 18:00","2020-09-22 09:00","2020-09-25 18:00","매일"]
[186,"경기","평택","오산평택#2 T/L","화성정남 전력구 운영시스템 설치공사","CCTV 및 PD진단 단자집합반 설치공사","2020-09-28 09:00","2020-09-29 18:00","2020-09-28 09:00","2020-09-29 18:00","매일"]
[187,"경기","평택","오산향남#2 T/L","화성정남 전력구 운영시스템 설치공사","CCTV 및 PD진단 단자집합반 설치공사","2020-09-28 09:00","2020-09-29 18:00","2020-09-28 09:00","2020-09-29 18:00","매일"]
[188,"경기","평택","오산평택#1 T/L","화성정남 전력구 운영시스템 설치공사","CCTV 및 PD진단 단자집합반 설치공사","2020-09-22 09:00","2020-09-25 18:00","2020-09-22 09:00","2020-09-25 18:00","매일"]
[189,"경기","평택","원정만호#1 T/L","20-21년 평택전력지사 송전정비회사 총액공사","SB담파 취부","2020-09-21 07:00","2020-09-22 18:00","2020-09-21 07:00","2020-09-22 18:00","연속"]
[190,"경기","평택","원정평택T/P#2 T/L","154kV 원정평택T/P T/L 인류클램프 점검","154kV 원정평택T/P T/L 인류클램프 점검","2020-09-28 12:00","2020-09-28 18:00","2020-09-28 12:00","2020-09-28 18:00","연속"]
[191,"경기","평택","원정평택T/P#1 T/L","154kV 원정평택T/P T/L 인류클램프 점검","154kV 원정평택T/P T/L 인류클램프 점검","2020-09-28 09:00","2020-09-28 12:00","2020-09-28 09:00","2020-09-28 12:00","연속"]
[192,"경기","평택","진위동탄#2 T/L","진위S/S 154kV #4M.Tr 증설 관련 최초가압 및 무부하가압","진위S/S 154kV #4M.Tr 증설 관련 최초가압 및 무부하가압","2020-09-14 09:00","2020-09-15 18:00","2020-09-14 09:00","2020-09-15 18:00","연속"]
[193,"경기","평택","청북평택#1 T/L","20-21 송전정비회사총액공사(피뢰기설치)","20-21 송전정비회사총액공사(피뢰기설치)","2020-09-19 07:00","2020-09-19 12:00","2020-09-19 07:00","2020-09-19 12:00","연속"]
[194,"경기","평택","청북평택#2 T/L","20-21 송전정비회사총액공사(SB댐퍼정비)","20-21 송전정비회사총액공사(SB댐퍼정비)","2020-09-19 12:00","2020-09-19 19:00","2020-09-19 12:00","2020-09-19 19:00","연속"]
[195,"경기","평택","둔포추팔#2 T/L","20-21 송전정비회사총액공사(피뢰기설치)","20-21 송전정비회사총액공사(피뢰기설치)","2020-09-16 07:00","2020-09-18 19:00","2020-09-16 07:00","2020-09-18 19:00","연속"]
[196,"경기","평택","둔포추팔#1 T/L","20-21 송전정비회사총액공사(안전이격확보)","20-21 송전정비회사총액공사(안전이격확보)","2020-09-16 07:00","2020-09-16 11:00","2020-09-16 07:00","2020-09-16 11:00","연속"]
[197,"경기","평택","오산평택#2 T/L","평택S/S 154kV 오산-평택#2T/L GCB 정밀점검","평택S/S 154kV 오산-평택#2T/L GCB 정밀점검 / 오산S/S 154kV 오산-평택#2T/L GIS 보통점검","2020-09-26 09:00","2020-09-27 18:00","2020-09-26 09:00","2020-09-27 18:00","연속"]
[198,"경기","평택","평택추팔#2 T/L","평택,추팔S/S 154kV 평택-추팔#2 T/L GCB,GIS 보통점검","평택,추팔S/S 154kV 평택-추팔#2 T/L GCB,GIS 보통점검","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[199,"경기","평택","평택TP평택CC#1 T/L","평택C/C 154kV 평택복합#1T/L GIS 보통점검 / 전자변 교체","평택C/C 154kV 평택복합#1T/L GIS 보통점검 / 전자변 교체","2020-09-24 10:00","2020-09-24 18:00","2020-09-24 10:00","2020-09-24 18:00","연속"]
[200,"경기","평택","평택TP평택CC#2 T/L","평택C/C 154kV 평택복합#2T/L GIS 보통점검 / 전자변 교체","평택C/C 154kV 평택복합#2T/L GIS 보통점검 / 전자변 교체","2020-09-25 10:00","2020-09-25 18:00","2020-09-25 10:00","2020-09-25 18:00","연속"]
[201,"강원","강릉","동해강릉 T/L","2020~21년도 송전정비회사 총액공사","- 154kV 강릉, 동해분기T/L SB댐퍼 교체 및 설치 - 154kV 강릉, 동해분기T/L 스페이서 교체 - 154kV 강릉, 동해분기T/L 성능저하 국산애자 교체","2020-09-15 08:00","2020-09-25 18:00","2020-09-15 08:00","2020-09-25 18:00","매일"]
[202,"강원","강릉","강릉영동TP T/L","2020~21년도 송전정비회사 총액공사","- 154kV 강릉T/L SB댐퍼 교체 및 설치 - 154kV 강릉T/L 스페이서 교체 - 154kV 강릉T/L 성능저하 국산애자 교체","2020-09-01 08:00","2020-09-11 18:00","2020-09-01 08:00","2020-09-11 18:00","매일"]
[203,"강원","강릉","신양양양양#2 T/L","2020년 170kV GIS 정밀점검","○ 2020년 170kV GIS 정밀점검","2020-09-21 10:00","2020-09-22 18:00","2020-09-21 10:00","2020-09-22 18:00","연속"]
[204,"강원","강릉","북평영동TP#1 T/L","2020년 170kV GIS 정밀점검","○ 2020년 170kV GIS 정밀점검","2020-09-14 10:00","2020-09-16 18:00","취소","취소","연속"]
[205,"강원","강릉","북평영동TP#2 T/L","2020년 170kV GIS 정밀점검","○ 2020년 170kV GIS 정밀점검","2020-09-17 10:00","2020-09-19 18:00","취소","취소","연속"]
[206,"강원","강릉","신제천주진#1 T/L","주진변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, AL시트패널 설치 등","2020-09-09 09:00","2020-09-11 18:00","2020-09-09 09:00","2020-09-11 18:00","매일"]
[207,"강원","강릉","주진평창#1 T/L","주진변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, AL시트패널 설치 등","2020-09-16 09:00","2020-09-22 18:00","2020-09-16 09:00","2020-09-22 18:00","매일"]
[208,"강원","강릉","주진평창#2 T/L","주진변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, AL시트패널 설치 등","2020-09-19 09:00","2020-09-25 18:00","2020-09-19 09:00","2020-09-25 18:00","매일"]
[209,"강원","강릉","신제천주진#2 T/L","주진변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, AL시트패널 설치 등","2020-09-23 09:00","2020-09-29 18:00","2020-09-23 09:00","2020-09-29 18:00","매일"]
[210,"강원","강릉","신제천주진#1 T/L","주진변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, AL시트패널 설치 등","2020-09-26 09:00","2020-09-29 18:00","2020-09-26 09:00","2020-09-29 18:00","매일"]
[211,"강원","동해","동해정선 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-16 08:00","2020-09-16 18:00","취소","취소","연속"]
[212,"강원","동해","동해동영월 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-15 08:00","2020-09-15 18:00","취소","취소","연속"]
[213,"강원","동해","동해T/P 154kV #2 BUS","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-09-24 09:00","2020-09-29 18:00","2020-09-24 09:00","2020-09-29 18:00","연속"]
[214,"강원","동해","삼척동해TP T/L","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-09-24 09:00","2020-10-23 18:00","2020-10-04 09:00","2020-10-28 18:00","연속"]
[215,"강원","동해","이원태백 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-24 08:00","2020-09-24 18:00","2020-09-24 08:00","2020-09-24 18:00","연속"]
[216,"강원","동해","이원도계 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-23 08:00","2020-09-23 18:00","2020-09-23 08:00","2020-09-23 18:00","연속"]
[217,"강원","동해","동해이원#2 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-22 08:00","2020-09-22 18:00","2020-09-22 08:00","2020-09-22 18:00","연속"]
[218,"강원","동해","동해이원#1 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-21 08:00","2020-09-21 18:00","2020-09-21 08:00","2020-09-21 18:00","연속"]
[219,"강원","동해","이원삼척 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-18 08:00","2020-09-18 18:00","취소","취소","연속"]
[220,"강원","동해","이원동해TP T/L","2020-21년 동해전력지사 송전정비회사 총액공사","국산애자교체","2020-09-17 08:00","2020-09-17 18:00","취소","취소","연속"]
[221,"강원","원주","신제천남원주#2 T/L","2020~2021년 원주전력지사 송전정비회사 총액공사","○ 성능저하 국산애자 교체(No.38,39,45)","2020-09-05 07:00","2020-09-05 18:00","취소","취소","연속"]
[222,"강원","원주","신제천남원주#1 T/L","2020~2021년 원주전력지사 송전정비회사 총액공사","○ 성능저하 국산애자 교체(No.38,39,45)","2020-09-04 07:00","2020-09-04 18:00","취소","취소","연속"]
[223,"강원","원주","횡성홍천#1 T/L","횡성변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, 샌드위치판넬, AL시트패널 설치 등","2020-09-26 09:00","2020-09-29 18:00","2020-09-26 09:00","2020-09-29 18:00","매일"]
[224,"강원","원주","횡성홍천#2 T/L","횡성변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, 샌드위치판넬, AL시트패널 설치 등","2020-09-23 09:00","2020-09-29 18:00","2020-09-23 09:00","2020-09-29 18:00","매일"]
[225,"강원","원주","북원주횡성#2 T/L","횡성변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, 샌드위치판넬, AL시트패널 설치 등","2020-09-19 09:00","2020-09-25 18:00","2020-09-19 09:00","2020-09-25 18:00","매일"]
[226,"강원","원주","북원주횡성#1 T/L","횡성변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, 샌드위치판넬, AL시트패널 설치 등","2020-09-15 09:00","2020-09-22 18:00","취소","취소","매일"]
[227,"강원","원주","횡성홍천#1 T/L","횡성변전소 외장재 교체공사","○ 공사목적 : 강원지역 잦은 산불발생에 따른 화재확산 방지 ○ 노후 외장재 철거 : 외벽 드라이비트 철거 등 ○ 외장재 설치 : 외벽 폴리메탈판넬, 샌드위치판넬, AL시트패널 설치 등","2020-09-09 09:00","2020-09-11 18:00","2020-09-09 09:00","2020-09-11 18:00","매일"]
[228,"강원","원주","북원주횡성#1 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV 장기사용 GIS 철거/설치 ㅇ 디지털화공사 케이블 철거 및 광케이블 포설 ㅇ SA 운영장치 시험","2020-09-01 08:00","2020-09-22 18:00","2020-09-01 08:00","2020-09-22 18:00","연속"]
[229,"강원","직할","청평HP의암HP T/L","가공송전 순시점검 위탁공사(피뢰기 설치대상개소 현장실측)","낙뢰고장 취약개소인 V련애자 취부철탑 피뢰기 설치를 위한 철탑부재규격 현장실측 휴전작업","2020-09-02 09:00","2020-09-02 18:00","취소","취소","연속"]
[230,"강원","직할","상남인제#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","섬락애자 교체 No.91 등 4기","2020-09-25 07:00","2020-09-25 18:00","2020-09-25 07:00","2020-09-25 18:00","연속"]
[231,"강원","직할","철원화천#1 T/L","2020~2021년 경기북부 직할 가공송전 정비회사 총액공사","ㅇ 154kV 운천-철원#1T/L 병가선로 - 압축인류크램프 및 점퍼선 교체","2020-09-22 08:00","2020-09-22 18:00","2020-09-22 08:00","2020-09-22 18:00","연속"]
[232,"강원","직할","운천철원#1 T/L","2020~2021년 경기북부 직할 가공송전 정비회사 총액공사","ㅇ 154kV 운천-철원#1T/L 병가선로 - 압축인류크램프 및 점퍼선 교체","2020-09-22 08:00","2020-09-22 18:00","2020-09-22 08:00","2020-09-22 18:00","연속"]
[233,"강원","직할","운천철원#2 T/L","20~21 강원본부 직할 변전정비 총액공사","○ 철원S/S 운천-철원#2T/L LA 보통점검 ○ 차단기 조작시험","2020-09-15 10:00","2020-09-15 18:00","2020-09-15 10:00","2020-09-15 18:00","연속"]
[234,"강원","직할","북춘천춘천HP T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV 북춘천-춘천HP T/L GCB, LA, PT 보통점검","2020-09-09 09:00","2020-09-09 18:00","취소","취소","연속"]
[235,"강원","직할","가평춘천HP T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV 가평-춘천HP T/L GCB, LA, PT 보통점검","2020-09-08 09:00","2020-09-08 18:00","취소","취소","연속"]
[236,"강원","직할","화천화천HP#2 T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","화천S/S 154kV 화천-화천HP #2 T/L 차단기 조작시험, LA 보통점검","2020-09-03 10:00","2020-09-03 18:00","2020-09-03 10:00","2020-09-03 18:00","연속"]
[237,"강원","직할","가평화천HP T/L","2020 강원직할 하반기 장기미동작 차단기 조작시험","○ 화천H/P 154kV 가평-화천H/P T/L 차단기 조작시험","2020-09-04 10:00","2020-09-04 14:00","취소","취소","연속"]
[238,"강원","직할","화천H/P 154kV #65 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #2 DS 보통점검 ○ #2 BUS CVT 보통점검","2020-09-02 14:00","2020-09-02 18:00","2020-09-02 14:00","2020-09-02 18:00","연속"]
[239,"강원","직할","화천H/P 154kV #60 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1 DS 보통점검 ○ #1 BUS CVT 보통점검","2020-09-02 10:00","2020-09-02 14:00","2020-09-02 10:00","2020-09-02 14:00","연속"]
[240,"강원","직할","화천화천HP#1 T/L","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1, 2 DS 보통점검","2020-09-02 10:00","2020-09-02 18:00","취소","취소","연속"]
[241,"강원","태백","고한영월 T/L","20~21년 태백전력지사 송전정비회사 총액공사","애자교체","2020-09-17 09:00","2020-09-17 18:00","취소","취소","연속"]
[242,"강원","태백","영월S/S 154kV CB 6100","20~21 태백전력지사 변전정비회사 총액공사","영월S/S 154kV BUS-TIE 휴전(모선보호반 원격 제어케이블 결선)","2020-09-25 10:00","2020-09-25 18:00","2020-09-25 10:00","2020-09-25 18:00","연속"]
[243,"강원","태백","영월S/S 154kV #2 BUS","'20~'21년 태백전력지사 변전정비회사 총액공사","영월변전소 모선보호반 원격제어케이블 결선작업","2020-09-25 10:00","2020-09-25 18:00","2020-09-25 10:00","2020-09-25 18:00","연속"]
[244,"강원","태백","태백영월 T/L","20~21년 태백전력지사 송전정비회사 총액공사","애자교체","2020-09-14 09:00","2020-09-16 18:00","취소","취소","매일"]
[245,"강원","태백","태백삼척GP#2 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거, 9.06(일) No.80에서 점퍼선 분리 후 태백S/S측에서 편단가압(T분기 고객 공급)","2020-09-06 09:00","2020-09-13 18:00","취소","취소","연속"]
[246,"강원","태백","태백삼척GP#1 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거","2020-09-06 09:00","2020-09-13 18:00","취소","취소","연속"]
[247,"강원","태백","태백고한 T/L","20~21년 태백전력지사 송전정비회사 총액공사","애자교체","2020-09-18 09:00","2020-09-18 18:00","취소","취소","연속"]
[248,"강원","원주","원주서원주#2 T/L","원주-서원주 #2T/L GIS 챔버 내부 점검","154kV 남원주-원주#1T/L 실부하 가압 중 고장으로 인한 잔여회선 추가 점검 시행","2020-09-07 09:00","2020-09-08 18:00","2020-09-07 09:00","2020-09-08 18:00","연속"]
[249,"강원","원주","원주북원주#1 T/L","원주-북원주 #1T/L GIS 챔버 내부 점검","154kV 남원주-원주#1T/L 실부하 가압 중 고장으로 인한 잔여회선 추가 점검 시행","2020-09-09 09:00","2020-09-10 18:00","2020-09-09 09:00","2020-09-10 18:00","연속"]
[250,"강원","원주","원주북원주#2 T/L","원주-북원주 #2T/L GIS 챔버 내부 점검","154kV 남원주-원주#1T/L 실부하 가압 중 고장으로 인한 잔여회선 추가 점검 시행","2020-09-11 09:00","2020-09-12 18:00","2020-09-11 09:00","2020-09-12 18:00","연속"]
[251,"충북","직할","삼죽광혜원 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼설치(4기),압축인류클램프교체(1기)","2020-09-18 08:00","2020-09-18 18:00","2020-09-18 08:00","2020-09-18 18:00","매일"]
[252,"충북","직할","서운광혜원 T/L","20~21년도 직할 변전정비회사 총액공사","서운-광혜원T/L 장기사용 배전반 대체","2020-09-21 10:00","2020-09-23 18:00","2020-09-21 10:00","2020-09-23 18:00","연속"]
[253,"충북","직할","남음성덕산#2 T/L","2020~21년 직할 송전정비회사 총액공사","불량애자교체(1기),항공장애표시등철거(1기)","2020-09-04 08:00","2020-09-04 18:00","2020-09-04 08:00","2020-09-04 18:00","매일"]
[254,"충북","직할","남음성덕산#1 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼설치(11기),항공장애표시등철거(1기)","2020-09-02 08:00","2020-09-03 18:00","2020-09-02 08:00","2020-09-03 18:00","매일"]
[255,"충북","직할","사리괴산 T/L","20~21년도 직할 변전정비회사 총액공사","사리S/S 154kV 사리-괴산T/L 하자점검","2020-09-24 10:00","2020-09-24 18:00","2020-09-24 10:00","2020-09-24 18:00","연속"]
[256,"충북","직할","사리초정#1 T/L","20~21년도 직할 변전정비회사 총액공사","사리S/S 154kV 사리-초정#1T/L 하자점검","2020-09-25 10:00","2020-09-25 18:00","2020-09-25 10:00","2020-09-25 18:00","연속"]
[257,"충북","직할","음성사리 T/L","20~21년도 직할 변전정비회사 총액공사","사리S/S 154kV 음성-사리T/L 하자점검","2020-09-28 10:00","2020-09-28 18:00","2020-09-28 10:00","2020-09-28 18:00","연속"]
[258,"충북","직할","신진천진천#1 T/L","20년도 충북본부 직할 154kV GIS 정밀점검공사","신진천-진천#1TL GIS 정밀점검","2020-09-05 09:00","2020-09-06 18:00","2020-09-19 08:00","2020-09-19 17:00","연속"]
[259,"충북","직할","신진천S/S 154kV CB 6100","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-07 09:00","2020-09-07 10:00","2020-09-07 09:00","2020-09-07 10:00","연속"]
[260,"충북","직할","신진천S/S 154kV SEC CB 60610","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-07 10:00","2020-09-07 11:00","2020-09-07 10:00","2020-09-07 11:00","연속"]
[261,"충북","직할","신진천S/S 154kV SEC CB 65660","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-07 11:00","2020-09-07 12:00","2020-09-07 11:00","2020-09-07 12:00","연속"]
[262,"충북","직할","신진천진천#2 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼설치(19기),불량애자교체(6기),피뢰기설치(2기)","2020-09-09 08:00","2020-09-13 18:00","취소","취소","매일"]
[263,"충북","직할","신진천S/S 154kV CB 6100","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-10 09:00","2020-09-10 10:00","2020-09-10 09:00","2020-09-10 10:00","연속"]
[264,"충북","직할","신진천S/S 154kV SEC CB 60610","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-10 10:00","2020-09-10 11:00","2020-09-10 10:00","2020-09-10 11:00","연속"]
[265,"충북","직할","신진천S/S 154kV SEC CB 60610","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #60-65 모선보호반 대체","2020-09-10 11:00","2020-09-10 12:00","2020-09-10 11:00","2020-09-10 12:00","연속"]
[266,"충북","직할","신진천오창#1 T/L","2020~21년 직할 송전정비회사 총액공사","154kV 신진천-진천#2T/L 작업에따른 안전이격확보","2020-09-12 08:00","2020-09-13 18:00","취속","취소","매일"]
[267,"충북","직할","신진천S/S 154kV #65 BUS","20년도 충북본부 직할 154kV GIS 정밀점검공사","#62M.Tr 1차 GIS 정밀점검 관련 무부하가압(#65BUS 휴전)","2020-09-13 15:00","2020-09-13 18:00","2020-09-06 14:00","2020-09-06 17:00","연속"]
[268,"충북","직할","신진천S/S 154kV CB 6200","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-14 09:00","2020-09-14 10:00","2020-09-14 09:00","2020-09-14 10:00","연속"]
[269,"충북","직할","신진천S/S 154kV SEC CB 60610","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-14 10:00","2020-09-14 11:00","2020-09-14 10:00","2020-09-14 11:00","연속"]
[270,"충북","직할","신진천S/S 154kV SEC CB 65660","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-14 11:00","2020-09-14 12:00","2020-09-14 11:00","2020-09-14 12:00","연속"]
[271,"충북","직할","신진천S/S 154kV SEC CB 61620","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-14 12:00","2020-09-14 13:00","2020-09-14 12:00","2020-09-14 13:00","연속"]
[272,"충북","직할","신진천S/S 154kV SEC CB 66670","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-14 13:00","2020-09-14 14:00","2020-09-14 13:00","2020-09-14 14:00","연속"]
[273,"충북","직할","신진천S/S 154kV CB 6200","장기 미동작 차단기 점검","동작특성 점검 기타부대작업","2020-09-05 09:00","2020-09-05 12:00","2020-09-05 09:00","2020-09-05 12:00","연속"]
[274,"충북","직할","신진천S/S 154kV SEC CB 60610","장기 미동작 차단기 점검","동작특성 점검 기타부대작업","2020-09-05 13:00","2020-09-05 15:00","2020-09-05 13:00","2020-09-05 15:00","연속"]
[275,"충북","직할","신진천S/S 154kV SEC CB 61620","장기 미동작 차단기 점검","동작특성 점검 기타부대작업","2020-09-05 15:00","2020-09-05 18:00","2020-09-05 15:00","2020-09-05 18:00","연속"]
[276,"충북","직할","신진천S/S 154kV #61 BUS","20년도 충북본부 직할 154kV GIS 정밀점검공사","신진천-진천#1T/L GIS 정밀점검 관련 무부하가압(#61BUS 휴전)","2020-09-06 14:00","2020-09-06 18:00","취소","취소","연속"]
[277,"충북","직할","신진천S/S 154kV #62 BUS","20년도 충북본부 직할 154kV GIS 정밀점검공사","#2Sh.C, #3 BUS TIE GIS 정밀점검 관련 무부하가압(#62BUS 휴전)","2020-09-06 15:00","2020-09-06 18:00","2020-09-03 14:00","2020-09-03 17:00","연속"]
[278,"충북","직할","신진천S/S 154kV CB 6200","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-17 09:00","2020-09-17 10:00","2020-09-17 09:00","2020-09-17 10:00","연속"]
[279,"충북","직할","신진천S/S 154kV SEC CB 60610","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-17 10:00","2020-09-17 11:00","2020-09-17 10:00","2020-09-17 11:00","연속"]
[280,"충북","직할","신진천S/S 154kV SEC CB 66670","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-17 13:00","2020-09-17 14:00","2020-09-17 13:00","2020-09-17 14:00","연속"]
[281,"충북","직할","신진천S/S 154kV SEC CB 61620","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-17 12:00","2020-09-17 13:00","2020-09-17 12:00","2020-09-17 13:00","연속"]
[282,"충북","직할","신진천S/S 154kV SEC CB 65660","20~21년도 직할 변전정비회사 총액공사","신진천S/S 154kV #61-66 모선보호반 대체","2020-09-17 11:00","2020-09-17 12:00","2020-09-17 11:00","2020-09-17 12:00","연속"]
[283,"충북","직할","진천광혜원#1 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","현수애자 절연성능진단 (중각도 철탑 2기)","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","매일"]
[284,"충북","직할","진천광혜원#2 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼(22기),압축인류클램프교체(2가닥),지지애자교체(2기),점퍼소켓교체","2020-09-14 08:00","2020-09-18 18:00","2020-09-14 08:00","2020-09-18 18:00","매일"]
[285,"충북","청주","국사봉명#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-09-19 07:00","2020-09-20 18:00","취소","취소","연속"]
[286,"충북","청주","국사봉명#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-09-30 07:00","2020-10-02 18:00","취소","취소","연속"]
[287,"충북","청주","국사봉명#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-09-26 07:00","2020-09-27 18:00","취소","취소","연속"]
[288,"충북","청주","남청주청주#1 T/L","20-21년 청주전력 변전정비회사 총액공사","남청주,청주S/S 154kV 남청주청주#1T/L 보호반 교체 공사","2020-09-28 09:00","2020-10-02 18:00","2020-09-28 09:00","2020-10-02 18:00","연속"]
[289,"충북","청주","상주보은 T/L","20-21년 청주전력 변전정비회사 총액공사","보은S/S 154kV 상주보은T/L GIS 보통점검","2020-09-11 09:30","2020-09-11 18:00","2020-09-11 09:30","2020-09-11 18:00","연속"]
[290,"충북","청주","신옥천남대전#3 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 154kV 신옥천남대전#3T/L GIS 초기점검","2020-09-04 09:30","2020-09-04 18:00","취소","취소","연속"]
[291,"충북","청주","신옥천남대전#2 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 154kV 신옥천남대전#2T/L GIS 초기점검","2020-09-03 09:30","2020-09-03 18:00","취소","취소","연속"]
[292,"충북","청주","신옥천남대전#1 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 154kV 신옥천남대전#1T/L GIS 초기점검","2020-09-02 09:30","2020-09-02 18:00","취소","취소","연속"]
[293,"충북","청주","신옥천남대전#4 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 154kV 신옥천남대전#4T/L GIS 초기점검","2020-09-08 09:30","2020-09-08 18:00","취소","취소","연속"]
[294,"충북","청주","오송북청주#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-09-26 07:00","2020-09-27 18:00","취소","취소","연속"]
[295,"충북","청주","오송북청주#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-09-30 07:00","2020-10-02 18:00","취소","취소","연속"]
[296,"충북","청주","오송북청주#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-09-19 07:00","2020-09-20 18:00","취소","취소","연속"]
[297,"충북","충주","점촌단양 T/L","20-21년 충주전력지사 변전정비 총액공사","공압식 차단기 전자변 교체 피뢰기 및 CVT 보통점검","2020-09-15 09:00","2020-09-15 14:00","취소","취소","연속"]
[298,"충북","충주","단양영월CC#1 T/L","20-21년 충주전력지사 변전정비 총액공사","공압식 차단기 전자변 교체(단양S/S) 피뢰기 및 CVT 보통점검(단양S/S)","2020-09-15 14:00","2020-09-15 18:00","2020-09-15 14:00","2020-09-15 18:00","연속"]
[299,"충북","충주","북충주충주 T/L","2020-2021년 송전정비회사 총액공사","압축인류클램프 교체 No.68,84,87,96,98,100,105,106,108,109,111,112 (12기)","2020-09-16 07:00","2020-09-23 18:00","2020-09-16 07:00","2020-09-23 18:00","매일"]
[300,"충북","충주","왕암가남#2 T/L","20-21년 충주전력지사 변전정비 총액공사","왕암가남#2T/L 인출 C상 접속단자 과열보수.","2020-09-03 10:00","2020-09-03 15:00","취소","취소","연속"]
[301,"충북","충주","왕암충주 T/L","2020-2021년 송전정비회사 총액공사","압축인류클램프 교체 (No.80,82,84,87,92,98,100,105,106,108,109,111,112(13기)","2020-09-07 07:00","2020-09-15 18:00","2020-09-07 07:00","2020-09-15 18:00","매일"]
[302,"충북","충주","왕암북충주 T/L","2020-2021년 송전정비회사 총액공사","현수애자 교체 (No.40)","2020-09-24 07:00","2020-09-24 18:00","2020-09-24 07:00","2020-09-24 18:00","연속"]
[303,"충북","충주","음성금왕#2 T/L","20-21년 충주전력지사 변전정비 총액공사","공압식 차단기 전자변 교체(음성S/S)","2020-09-12 14:00","2020-09-12 18:00","2020-09-12 14:00","2020-09-12 18:00","연속"]
[304,"충북","충주","음성금왕#1 T/L","20-21년 충주전력지사 변전정비 총액공사","공압식 차단기 전자변 교체(음성S/S) 피뢰기 점검","2020-09-12 10:00","2020-09-12 14:00","2020-09-12 10:00","2020-09-12 14:00","연속"]
[305,"대전충남","대전","논산은진#1 T/L","은진S/S 154kV 변전철구 철거공사","은진S/S 154kV 변전철구 철거공사 [병행] 논산S/S 154kV 논산-은진#1T/L GIS 및 LA 보통점검","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[306,"대전충남","대전","논산은진#2 T/L","은진S/S 154kV 변전철구 철거공사","은진S/S 154kV 변전철구 철거공사","2020-09-21 09:00","2020-09-21 10:30","취소","취소","연속"]
[307,"대전충남","세종","부강월산#2 T/L","[송전]154kV 부강-월산T/L 지장송전선로 이설공사","○ 공사구간 : 154kV 부강-월산T/L No.28~36 ○ 지지물 : 9기 설치, 6기 철거 ○ 전력선 : ACSR 410 x 2B x 2C, 3.434km(신설) 1.803km(철거)","2020-09-01 07:00","2020-09-04 18:00","2020-09-01 07:00","2020-09-04 18:00","연속"]
[308,"대전충남","세종","부강월산#2 T/L","[송전]154kV 부강-월산T/L 지장송전선로 이설공사","○ 공사구간 : 154kV 부강-월산T/L No.28~36 ○ 지지물 : 9기 설치, 6기 철거 ○ 전력선 : ACSR 410 x 2B x 2C, 3.434km(신설) 1.803km(철거)","2020-09-14 07:00","2020-09-20 18:00","2020-09-14 07:00","2020-09-20 18:00","연속"]
[309,"대전충남","세종","부강월산#1 T/L","[송전]154kV 부강-월산T/L 지장송전선로 이설공사","○ 공사구간 : 154kV 부강-월산T/L No.28~36 ○ 지지물 : 9기 설치, 6기 철거 ○ 전력선 : ACSR 410 x 2B x 2C, 3.434km(신설) 1.803km(철거)","2020-09-21 07:00","2020-09-29 18:00","2020-09-21 07:00","2020-09-29 18:00","연속"]
[310,"대전충남","세종","조치원월산 T/L","'20년 170kV GIS 정밀점검공사","○170kV GIS 정밀점검공사","2020-09-23 09:00","2020-09-24 18:00","2020-09-23 09:00","2020-09-24 18:00","연속"]
[311,"대전충남","세종","천안전의#1 T/L","[변전]세종PO변전총액공사","천안-전의#1T/L 피뢰기 하자점검","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[312,"대전충남","세종","천안전의#2 T/L","[변전]세종PO변전총액공사","천안-전의#2T/L 피뢰기 하자점검","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[313,"대전충남","세종","서세종조치원 T/L","'20년 170kV GIS 정밀점검공사","○170kV GIS 정밀점검공사","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[314,"대전충남","아산","불당서천안#1 T/L","불당S/S 불당-서천안#1T/L CB 전자변 교체","불당S/S 불당-서천안#1T/L CB 전자변 교체","2020-09-09 09:00","2020-09-09 18:00","취소","취소","연속"]
[315,"대전충남","아산","불당서천안#2 T/L","불당S/S 불당-서천안#2T/L CB 전자변 교체","불당S/S 불당-서천안#2T/L CB 전자변 교체","2020-09-10 09:00","2020-09-10 18:00","취소","취소","연속"]
[316,"대전충남","아산","신탕정탕정#1 T/L","신탕정,탕정S/S 154kV 신탕정-탕정#1T/L GIS 보통점검","신탕정,탕정S/S 154kV 신탕정-탕정#1T/L GIS 보통점검, 전자변 교체, 보호배전반 성능개선","2020-09-07 09:00","2020-09-07 18:00","취소","취소","연속"]
[317,"대전충남","아산","신탕정탕정#2 T/L","신탕정,탕정S/S 154kV 신탕정-탕정#2T/L GIS 보통점검","신탕정,탕정S/S 154kV 신탕정-탕정#2T/L GIS 보통점검, 전자변 교체, 보호배전반 성능개선","2020-09-08 09:00","2020-09-08 18:00","취소","취소","연속"]
[318,"대전충남","아산","아산온양#1 T/L","[송전]154kV아산-온양#1T/L 과열개소 정비","154kV아산-온양#1T/L No.34-1 과열개소 정비","2020-09-19 08:00","2020-09-19 13:00","2020-09-19 08:00","2020-09-19 13:00","연속"]
[319,"대전충남","아산","온양풍세#2 T/L","온양,풍세S/S 154kV 온양-풍세#2T/L 보호배전반 교체","온양,풍세S/S 154kV 온양-풍세#2T/L 보호배전반 교체","2020-09-21 09:00","2020-09-24 18:00","2020-09-21 09:00","2020-09-24 18:00","연속"]
[320,"대전충남","아산","장재천안#1 T/L","[송전]154kV 장재-천안#1,2T/L No.24~25 지중화공사","천안시 청당지구 지중화 사업요청에 의한 154kV 장재-천안#1,2T/L No.24~25 일부구간 지중화 (0.573km)","2020-09-21 08:00","2020-12-31 18:00","취소","취소","연속"]
[321,"대전충남","아산","장재천안#2 T/L","[송전]154kV 장재-천안#1,2T/L No.24~25 지중화공사","천안시 청당지구 지중화 사업요청에 의한 154kV 장재-천안#1,2T/L No.24~25 일부구간 지중화 (0.573km)","2020-09-21 08:00","2020-12-31 18:00","2020-09-21 08:00","2020-10-28 18:00","연속"]
[322,"대전충남","청양","신서천대천#1 T/L","청양P/O 관내 OPGW 항공장애표시구 시설공사","3경간 항공구 33개 시설(No.19~22호)","2020-09-03 07:00","2020-09-04 18:00","2020-09-03 07:00","2020-09-04 18:00","연속"]
[323,"대전충남","청양","신서천대천#2 T/L","대천S/S 170kV GCB 전자변 교체","대천S/S 170kV GCB 전자변 교체","2020-09-02 08:00","2020-09-02 18:00","2020-09-02 08:00","2020-09-02 18:00","연속"]
[324,"대전충남","청양","신서천옥산#2 T/L","154kV 옥산-서천T/L 애자교체","No.10호 상단 전원 내측 애자 교체","2020-09-02 08:00","2020-09-02 18:00","2020-09-02 08:00","2020-09-02 18:00","연속"]
[325,"대전충남","청양","신서천옥산#1 T/L","청양P/O 관내 OPGW 항공장애표시구 시설공사","3경간 항공구 33개 시설(No.19~22호)","2020-09-03 07:00","2020-09-04 18:00","2020-09-03 07:00","2020-09-04 18:00","연속"]
[326,"전북","군산","군공군산CC#2 T/L","군산P/O 154kV이상 차단기 조작시험공사","-군공S/S 군공-군산복합#2T/L 차단기 조작시험 -군산복합CC 군공-군산복합#2T/L 차단기 조작시험","2020-09-01 13:00","2020-09-01 16:00","2020-09-01 13:00","2020-09-01 16:00","연속"]
[327,"전북","군산","군공군산CC#1 T/L","군산P/O 154kV이상 차단기 조작시험공사","- 군공S/S 군공-군산복합#1T/L 차단기 조작시험 - 군산복합CC 군공-군산복합#1T/L 차단기 조작시험","2020-09-01 09:00","2020-09-01 13:00","2020-09-01 09:00","2020-09-01 13:00","연속"]
[328,"전북","군산","군산S/S 154kV SEC CB 66650","군산P/O 154kV이상 차단기 점검공사","-군산S/S 154kV #65-#66 SEC 차단기 점검공사","2020-09-02 09:00","2020-09-02 14:00","2020-09-02 09:00","2020-09-02 14:00","연속"]
[329,"전북","군산","군산동군산#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-02 09:00","2020-09-02 18:00","2020-09-02 09:00","2020-09-02 18:00","연속"]
[330,"전북","군산","군산동군산#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-03 09:00","2020-09-03 18:00","2020-09-03 09:00","2020-09-03 18:00","연속"]
[331,"전북","군산","군산이리#2 T/L","154kV 군산-이리T/L 안전이격확보공사","18,19호 가철탑 조립 및 공중이동","2020-09-06 07:00","2020-09-09 18:00","2020-09-06 07:00","2020-09-09 18:00","연속"]
[332,"전북","군산","군산이리#1 T/L","154kV 군산-이리T/L 안전이격확보공사","18,19호 가철탑 조립 및 공중이동","2020-09-01 07:00","2020-09-05 18:00","2020-09-01 07:00","2020-09-05 18:00","연속"]
[333,"전북","군산","군산영등#2 T/L","성능저하 국산 점퍼지지애자 교체공사","-점퍼지지애자교체 : S/T, 44, 55호","2020-09-15 07:00","2020-09-15 18:00","2020-09-29 07:00","2020-09-29 18:00","연속"]
[334,"전북","군산","군산영등#1 T/L","성능저하 국산 점퍼지지애자 교체공사","-점퍼지지애자교체 : S/T, 44, 55호","2020-09-14 07:00","2020-09-14 18:00","2020-09-28 07:00","2020-09-28 18:00","연속"]
[335,"전북","군산","군산S/S 154kV SEC CB 67660","군산P/O 154kV이상 차단기 조작시험공사","-군산S/S 154kV #66-#67 SEC 차단기 조작시험","2020-09-02 14:00","2020-09-02 16:00","2020-09-02 14:00","2020-09-02 16:00","연속"]
[336,"전북","군산","군산서군산#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-09 09:00","2020-09-09 18:00","2020-09-09 09:00","2020-09-09 18:00","연속"]
[337,"전북","군산","군산서군산#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-08 09:00","2020-09-08 18:00","2020-09-08 09:00","2020-09-08 18:00","연속"]
[338,"전북","군산","비응군장#1 T/L","'20년도 군산P/O 170kV GIS 정밀점검공사","-군장S/S 154kV 비응-군장#1T/L GIS 정밀점검","2020-09-07 09:00","2020-09-08 18:00","취소","취소","연속"]
[339,"전북","군산","비응군장#2 T/L","'20년도 군산P/O 170kV GIS 정밀점검공사","-군장S/S 비응-군장#2T/L GIS 정밀점검","2020-09-09 09:00","2020-09-10 18:00","취소","취소","연속"]
[340,"전북","군산","내초군장#2 T/L","내초S/S #3M.Tr 부분방전 해소공사 무부하 가압","- 내초S/S #3M.Tr 부분방전 해소 내부점검 후 무부하 가압","2020-09-05 09:00","2020-09-05 18:00","2020-09-05 09:00","2020-09-05 18:00","연속"]
[341,"전북","군산","비응군장#1 T/L ","비응S/S 170kV GIS 제작사 부분방전 하자보수공사","GIS 이음발생 하자보수 2DS 이음개소 하자보수","2020-09-21 09:00","2020-09-25 18:00","취소","취소","연속"]
[342,"전북","군산","새만금비응#1 T/L ","비응S/S 170kV GIS 제작사 부분방전 하자보수공사","GIS 이음발생 하자보수 2DS 이음개소 하자보수","2020-09-21 09:00","2020-09-25 18:00","취소","취소","연속"]
[343,"전북","군산","비응군장#2T/L ","비응S/S 154kV GIS 제작사 부분방전 관련 하자보수공사","차단부 부분방전 하자보수 2DS 이음개소 하자보수","2020-09-14 09:00","2020-09-18 18:00","취소","취소","연속"]
[344,"전북","군산","새만금비응#2 T/L ","비응S/S 154kV GIS 제작사 부분방전 관련 하자보수공사","차단부 부분방전 하자보수 2DS 이음개소 하자보수","2020-09-14 09:00","2020-09-18 18:00","취소","취소","연속"]
[345,"전북","군산","서군산소룡#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-15 09:00","2020-09-15 18:00","2020-09-15 09:00","2020-09-15 18:00","연속"]
[346,"전북","군산","서군산소룡#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[347,"전북","군산","영등팔봉#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-07 09:00","2020-09-07 18:00","2020-09-06 09:00","2020-09-06 18:00","연속"]
[348,"전북","군산","영등팔봉#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-04 09:00","2020-09-04 18:00","2020-09-05 09:00","2020-09-05 18:00","연속"]
[349,"전북","군산","이리백산#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[350,"전북","군산","이리백산#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-18 09:00","2020-09-18 18:00","2020-09-18 09:00","2020-09-18 18:00","연속"]
[351,"전북","군산","팔봉봉동#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-17 09:00","2020-09-17 18:00","2020-09-13 09:00","2020-09-13 18:00","연속"]
[352,"전북","군산","팔봉두마#2 T/L","군산P/O 154kV이상 차단기 조작시험","-팔봉S/S 팔봉-두마#2T/L 차단기 조작시험","2020-09-15 09:30","2020-09-15 12:00","2020-09-15 09:30","2020-09-15 12:00","연속"]
[353,"전북","군산","팔봉봉동#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-16 09:00","2020-09-16 18:00","2020-09-12 09:00","2020-09-12 18:00","연속"]
[354,"전북","군산","팔봉두마#1 T/L","성능저하 국산 점퍼지지애자 교체공사","-점퍼지지애자교체 : 7호","2020-09-18 07:00","2020-09-18 18:00","2020-09-18 07:00","2020-09-18 18:00","연속"]
[355,"전북","김제","김제부안#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[356,"전북","김제","김제칠보HP T/L","154kV 신김제-전주 등 15개 T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-29 09:00","2020-09-29 18:00","취소","취소","연속"]
[357,"전북","김제","담양김제 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사",". 공사개요 □ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-28 09:00","2020-09-28 18:00","2020-09-28 09:00","2020-09-28 18:00","연속"]
[358,"전북","김제","김제부안#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-22 09:00","2020-09-22 18:00","2020-09-22 09:00","2020-09-22 18:00","연속"]
[359,"전북","김제","신김제남전주#2 T/L ","남전주S/S 신김제-남전주#2T/L 87 RY 교체","남전주S/S 신김제-남전주#2T/L 87 RY 교체","2020-09-09 13:00","2020-09-09 15:00","2020-09-09 13:00","2020-09-09 15:00","연속"]
[360,"전북","김제","김제칠보HP T/L ","RTU FLOATING 불량 관련 회로 변경","RTU FLOATING 불량 관련 회로 변경","2020-09-01 09:00","2020-09-01 12:00","2020-09-01 09:00","2020-09-01 12:00","연속"]
[361,"전북","김제","정공칠보HP T/L ","RTU FLOATING 불량 관련 회로 변경","RTU FLOATING 불량 관련 회로 변경","2020-09-01 13:00","2020-09-01 15:00","2020-09-01 13:00","2020-09-01 15:00","연속"]
[362,"전북","김제","신김제S/S 154kV CB 6100","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (MAIN 교체)","2020-09-01 09:00","2020-09-23 18:00","2020-09-01 09:00","2020-09-23 18:00","연속"]
[363,"전북","김제","신김제S/S 154kV #60 BUS","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 ","2020-09-06 18:00","2020-09-14 18:00","2020-09-06 18:00","2020-09-14 18:00","연속"]
[364,"전북","김제","신김제동전주#1 T/L","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-06 09:00","2020-09-06 18:00","취소","취소","연속"]
[365,"전북","김제","신김제S/S 154kV SEC CB 60610","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 ","2020-09-06 18:00","2020-09-14 18:00","2020-09-06 18:00","2020-09-14 18:00","연속"]
[366,"전북","김제","신김제동전주#1 T/L","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-14 09:00","2020-09-14 18:00","취소","취소","연속"]
[367,"전북","김제","신김제S/S 154kV #65 BUS","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 ","2020-09-14 18:00","2020-09-23 18:00","2020-09-14 18:00","2020-09-23 18:00","연속"]
[368,"전북","김제","신김제동전주#1 T/L","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-23 09:00","2020-09-23 18:00","취소","취소","연속"]
[369,"전북","김제","신김제남전주#1 T/L","신김제S/S 노후 170GIS 교체공사(동전주TL 시송불가시 활용)","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-06 09:00","2020-09-06 18:00","2020-09-06 09:00","2020-09-06 18:00","연속"]
[370,"전북","김제","신김제남전주#1 T/L","신김제S/S 노후 170GIS 교체공사(동전주TL 시송불가시 활용)","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[371,"전북","김제","신김제S/S 154kV SEC CB 65660","신김제S/S 노후 170GIS 교체공사(동전주TL 시송불가시 활용)","장기사용 노후 170GIS 교체공사 ","2020-09-06 09:00","2020-09-23 18:00","2020-09-01 09:00","2020-09-06 18:00","연속"]
[372,"전북","김제","신김제남전주#1 T/L","신김제S/S 노후 170GIS 교체공사(동전주TL 시송불가시 활용)","장기사용 노후 170GIS 교체공사 (시험가압 / 신김제동전주#1 과 신김제남전주#1 둘중하나 가능)","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[373,"전북","김제","신김제전주#1 T/L","관내S/S 154kV 이상 차단기 조작시험","관내S/S 154kV 이상 차단기 조작시험","2020-09-14 10:00","2020-09-14 14:00","취소","취소","연속"]
[374,"전북","김제","신김제전주#2 T/L","관내S/S 154kV 이상 차단기 조작시험","관내S/S 154kV 이상 차단기 조작시험","2020-09-14 14:00","2020-09-14 18:00","취소","취소","연속"]
[375,"전북","김제","신김제S/S 154kV #65 BUS","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 ","2020-09-01 09:00","2020-09-06 18:00","2020-09-01 09:00","2020-09-06 18:00","연속"]
[376,"전북","김제","신김제S/S 154kV #66 BUS","신김제S/S 노후 170GIS 교체공사","장기사용 노후 170GIS 교체공사  (시험가압시 필요)","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[377,"전북","김제","신김제S/S 154kV #61 BUS","신김제S/S 노후 170GIS 교체공사","장기사용 노후 170GIS 교체공사  (시험가압시 필요)","2020-09-14 09:00","2020-09-14 18:00","2020-09-14 09:00","2020-09-14 18:00","연속"]
[378,"전북","김제","신김제정공#1 T/L","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 (MAIN 교체)","2020-09-01 09:00","2020-09-23 18:00","2020-09-01 09:00","2020-09-23 18:00","연속"]
[379,"전북","김제","신김제S/S 154kV #66 BUS","신김제S/S 노후 170GIS 교체공사","장기사용 노후 170GIS 교체공사  (시험가압시 필요)","2020-09-06 09:00","2020-09-06 18:00","2020-09-06 09:00","2020-09-06 18:00","연속"]
[380,"전북","김제","정공담양 T/L","관내S/S 154kV 이상 차단기 조작시험","관내S/S 154kV 이상 차단기 조작시험","2020-09-07 10:00","2020-09-07 12:00","2020-09-07 10:00","2020-09-07 12:00","연속"]
[381,"전북","직할","남원임실#2 T/L","154kV 남원-임실#2T/L OPGW 증설공사","가공지선 철거후 OPGW 교체","2020-09-01 07:00","2020-09-19 18:00","2020-09-01 07:00","2020-09-19 18:00","연속"]
[382,"전북","직할","신김제전주#1 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[383,"전북","직할","신김제전주#2 T/L","154kV 신김제-전주 등 15개T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[384,"전북","직할","이리탄소#1 T/L","154kV 탄소분기 지중T/L 접속함 내부점검","154kV 이리-탄소#1T/L J/B#8 A상 접속함 내부점검","2020-09-14 10:00","2020-09-18 18:00","2020-09-14 10:00","2020-09-18 18:00","연속"]
[385,"전북","직할","전주탄소#1 T/L","154kV 탄소분기 지중T/L 접속함 내부점검","154kV 탄소-전주#1T/L M/H#5 B상 접속함 내부점검","2020-09-14 10:00","2020-09-18 18:00","2020-09-14 10:00","2020-09-18 18:00","연속"]
[386,"광주전남","강진","신강진대불#1 T/L","154kV 대불-남악 등 5개 T/L 아킹혼 설치공사 안전이격확보","No.1~64호 중 27기","2020-09-14 08:00","2020-09-15 18:00","2020-09-27 08:00","2020-09-29 18:00","매일"]
[387,"광주전남","강진","신강진대불#2 T/L","154kV 대불-남악 등 5개 T/L 아킹혼 설치공사 안전거리확보","No.1~64호 중 16기","2020-09-16 08:00","2020-09-16 18:00","2020-09-25 08:00","2020-09-26 18:00","연속"]
[388,"광주전남","강진","장흥보성 T/L","장흥S/S 장기사용 GIS 대체공사","154kV #60-65BUS PT GIS 설치 154kV #60-65BUS TIE GIS 설치","2020-09-01 09:00","2020-09-13 18:00","취소","취소","연속"]
[389,"광주전남","강진","장흥벌교 T/L","장흥S/S 장기사용 GIS 대체공사","GIS 대체관련 안전 이격거리 확보","2020-09-01 09:00","2020-09-02 18:00","취소","취소","매일"]
[390,"광주전남","강진","장흥벌교 T/L","장흥S/S 장기사용 GIS 대체공사","GIS 대체관련 안전 이격거리 확보","2020-09-07 09:00","2020-09-08 18:00","2020-09-05 09:00","2020-09-06 18:00","매일"]
[391,"광주전남","강진","강진장흥#2 T/L","장흥S/S 장기사용 GIS 대체공사","강진-장흥#2T/L GIS 대체 #60-65BUS PT GIS 철거 #60-65BUS TIE GIS 철거","2020-09-14 09:00","2020-09-29 18:00","2020-09-14 09:00","2020-09-29 18:00","연속"]
[392,"광주전남","강진","제주#1HVDC #2Pole CB (해남CS제주C/S#2 T/L)","`20~21년 #1HVDC 변환설비 위탁정비공사","변환설비 연차점검(Valve, C.Tr, AC Filter, 공조설비, 냉각설비, 제어설비)","2020-09-05 09:00","2020-09-24 18:00","2020-09-05 09:00","2020-09-24 18:00","연속"]
[393,"광주전남","강진","제주#1HVDC #1Pole CB (해남CS제주C/S#1 T/L)","`20~21년 #1HVDC 변환설비 위탁정비공사","변환설비 연차점검(Valve, C.Tr, AC Filter, 공조설비, 냉각설비, 제어설비)","2020-09-01 09:00","2020-09-24 18:00","2020-09-01 09:00","2020-09-24 18:00","연속"]
[394,"광주전남","광주","신광주일곡#1 T/L","154kV 신광주-일곡T/L No.11호 국산애자 교체","154kV 신광주-일곡T/L No.11호 국산애자 교체","2020-09-21 09:00","2020-09-21 18:00","취소","취소","연속"]
[395,"광주전남","목포","장성영광#1 T/L","154kV 남악-북항 등 5개 T/L 아킹혼 설치공사","No.125,126,127,136,150,160","2020-09-07 08:00","2020-09-07 14:00","2020-09-07 08:00","2020-09-10 14:00","연속"]
[396,"광주전남","목포","장성영광#2 T/L","154kV 장성-영광 #2 T/L 애자교체공사","No.125","2020-09-10 14:00","2020-09-11 18:00","2020-09-10 14:00","2020-09-11 18:00","연속"]
[397,"광주전남","목포","고창영광 T/L","영광S/S 170kV GIS 신규수용공사(함구미)","함구미태양광T/L 증설관련 T/L 무부하가압","2020-09-18 09:00","2020-09-19 18:00","2020-09-18 09:00","2020-09-19 18:00","연속"]
[398,"광주전남","목포","영광홍농 T/L","154kV 남악-북항 등 5개 T/L 아킹혼 설치공사 안전이격확보","No.126,127,136,150,160 아킹혼 설치공사 안전이격 확보","2020-09-07 08:00","2020-09-07 14:00","2020-09-07 08:00","2020-09-07 14:00","연속"]
[399,"광주전남","순천","광양하동#1 T/L","154kV 광양-하동#1 T/L 정밀점검","20년도 가공송전 순시점검 위탁공사 - 광양-하동#1 T/L 정밀점검 : No.38~91호(53기)","2020-09-21 08:00","2020-09-22 18:00","취소","취소","매일"]
[400,"광주전남","순천","광양하동#2 T/L","154kV 광양-하동#2 T/L 정밀점검","20년도 가공송전 순시점검 위탁공사 - 광양-하동#2 T/L 정밀점검 : No.38~91호(53기)","2020-09-23 08:00","2020-09-24 18:00","취소","취소","매일"]
[401,"광주전남","순천","여수소라#2 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여수,소라S/S 여수-소라#2T/L 송전선로 보호반 대체","2020-09-21 09:00","2020-09-23 18:00","취소","취소","연속"]
[402,"광주전남","순천","여수T/P 154kV #65 BUS","여수화력S/Y #4M.Tr 및 SW 증설공사","345kV #4M.Tr 및 광양CC-여수TP #1,2T/L 증설","2020-09-21 09:00","2020-09-25 18:00","2020-09-21 09:00","2020-09-25 18:00","연속"]
[403,"광주전남","순천","여수T/P 154kV #60 BUS","여수화력S/Y #4M.Tr 및 SW 증설공사","345kV #4M.Tr 및 광양CC-여수TP #1,2T/L 증설","2020-09-14 09:00","2020-09-18 18:00","2020-09-14 09:00","2020-09-18 18:00","연속"]
[404,"광주전남","순천","여천여수산단#1 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여천S/S 여천-여수산단#1T/L GIS 타임측정","2020-09-09 09:00","2020-09-09 18:00","2020-09-09 09:00","2020-09-09 18:00","연속"]
[405,"광주전남","순천","여수TP여천#2 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여천S/S 여수TP-여천#2T/L GIS 타임측정","2020-09-28 14:00","2020-09-28 18:00","2020-09-28 14:00","2020-09-28 18:00","연속"]
[406,"광주전남","순천","여수TP여천#1 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여천S/S 여수TP-여천#1T/L LA(A,C) 하자점검 및 타임측정","2020-09-28 09:00","2020-09-28 14:00","2020-09-28 09:00","2020-09-28 14:00","연속"]
[407,"광주전남","순천","순천율촌#1 T/L","20-21년 순천전력지사 변전정비회사 총액공사","율촌S/S 순천-율촌#1T/L LA(A,B,C)상 하자점검 및 GIS 보통점검","2020-09-18 09:00","2020-09-18 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[408,"광주전남","직할","남광주금천#1 T/L","EB-A 부분방전 진단센서 설치공사","UWB센서 및 PD집합반 설치","2020-09-22 09:00","2020-09-22 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[409,"광주전남","직할","충장농성#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체","2020-09-07 09:00","2020-10-09 18:00","2020-09-07 09:00","2020-10-09 18:00","연속"]
[410,"광주전남","직할","농성화정#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체관련 무부하선로","2020-09-07 15:00","2020-09-07 16:00","2020-09-07 15:00","2020-09-07 16:00","연속"]
[411,"광주전남","직할","농성화정#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체관련 무부하선로","2020-09-08 09:00","2020-09-08 10:00","2020-09-08 09:00","2020-09-08 10:00","연속"]
[412,"광주전남","직할","왕곡나주#1 T/L","왕곡 변전기자재 실증시험장 신축공사","선로인접구간 실리콘 마무리 작업","2020-09-14 09:00","2020-09-15 18:00","2020-09-14 09:00","2020-09-15 18:00","연속"]
[413,"광주전남","직할","왕곡나주#2 T/L","2020~21년 광주전남본부 직할 변전정비회사 총액공사","170kV GIS 초기점검","2020-09-21 09:00","2020-09-21 14:00","2020-09-21 09:00","2020-09-21 14:00","연속"]
[414,"광주전남","직할","평동왕곡#2 T/L","2020~21년 광주전남본부 직할 변전정비회사 총액공사","170kV GIS 초기점검","2020-09-21 14:00","2020-09-21 18:00","2020-09-21 14:00","2020-09-21 18:00","연속"]
[415,"광주전남","직할","평동왕곡#1 T/L","왕곡 변전기자재 실증시험장 신축공사","선로인접구간 실리콘 마무리 작업","2020-09-14 09:00","2020-09-15 18:00","2020-09-14 09:00","2020-09-15 18:00","연속"]
[416,"광주전남","직할","하남평동#1 T/L","154kV 덕림분기 T/L 건설공사","전력선 가선공사(하남평동T/L No.7~ 덕림분기T/L No.33호, 13.7km)","2020-09-24 09:00","2020-09-29 18:00","2020-09-24 09:00","2020-09-29 18:00","연속"]
[417,"광주전남","직할","하남평동#2 T/L","154kV 덕림분기 T/L 건설공사","전력선 가선공사(하남평동T/L No.7~ 덕림분기T/L No.33호, 13.7km)","2020-09-24 09:00","2020-09-29 18:00","2020-09-24 09:00","2020-09-29 18:00","연속"]
[418,"광주전남","직할","농성화정#1 T/L","2020년 직할 관내 170kV GIS 정밀점검 공사","ㅇ 170kV GIS 정밀점검","2020-09-21 09:00","2020-09-23 12:00","2020-09-21 09:00","2020-09-23 12:00","연속"]
[419,"대구","경산","대구범물#2 T/L","20~21년 경산전력지사 변전정비회사 총액공사","- 공기압력계 교체","2020-09-28 09:30","2020-09-28 11:30","2020-09-28 09:30","2020-09-28 11:30","연속"]
[420,"대구","경산","신경산진량 T/L","2020~21년 경산변전협력 총액공사","장기미동작 조작시험","2020-09-23 09:30","2020-09-23 18:00","2020-09-23 09:30","2020-09-23 18:00","연속"]
[421,"대구","경산","청도밀양#2 T/L","154kV 대구-청도T/L 용량증대 전선교체공사","대구-청도T/L 용량증대 전선교체 관련 병가구간 안전확보 교체구간:대구S/T ~ 청도S/T","2020-09-12 07:00","2020-09-19 18:00","2020-09-12 07:00","2020-09-19 18:00","연속"]
[422,"대구","경산","청도밀양#1 T/L","154kV 대구-청도T/L 용량증대 전선교체공사","대구-청도T/L 용량증대 전선교체 관련 병가구간 안전확보 교체구간:대구S/T ~ 청도S/T","2020-09-20 07:00","2020-09-27 18:00","2020-09-20 07:00","2020-09-27 18:00","연속"]
[423,"대구","달성","다산강창#1 T/L","강창S/S 154kV 다산-강창#1T/L 차단기 동작시험","강창S/S 154kV 다산-강창#1T/L 차단기 동작시험","2020-09-11 09:00","2020-09-11 14:00","2020-09-11 09:00","2020-09-11 14:00","연속"]
[424,"대구","달성","다산강창#2 T/L","강창S/S 154kV 다산-강창#2T/L 전자변교체","강창S/S 154kV 다산-강창#2T/L 전자변교체","2020-09-11 14:00","2020-09-11 18:00","2020-09-11 14:00","2020-09-11 18:00","연속"]
[425,"대구","달성","고령S/S 154kV #66 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-18 17:00","2020-09-18 18:00","취소","취소","연속"]
[426,"대구","달성","고령다산#2 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-15 08:00","2020-09-19 18:00","취소","취소","연속"]
[427,"대구","달성","고령쌍림#2 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-15 08:00","2020-09-20 18:00","취소","취소","연속"]
[428,"대구","달성","고령다산#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-14 14:00","2020-09-14 18:00","취소","취소","연속"]
[429,"대구","달성","고령쌍림#2 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-14 11:00","2020-09-14 14:00","취소","취소","연속"]
[430,"대구","달성","고령쌍림#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-14 09:00","2020-09-14 11:00","취소","취소","연속"]
[431,"대구","달성","고령다산#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-20 08:00","2020-09-24 18:00","취소","취소","연속"]
[432,"대구","달성","고령쌍림#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-20 08:00","2020-09-23 18:00","취소","취소","연속"]
[433,"대구","달성","고령S/S 154kV #61 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-23 17:00","2020-09-23 18:00","취소","취소","연속"]
[434,"대구","달성","고령S/S 154kV #60 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-23 18:00","2020-09-24 18:00","취소","취소","연속"]
[435,"대구","달성","고령논공#1 T/L","지중송전 피뢰기 열화진단","154kV 고령-논공#1T/L C/H 피뢰기 열화진단","2020-09-26 09:00","2020-09-26 14:00","2020-09-26 09:00","2020-09-26 14:00","연속"]
[436,"대구","달성","고령논공#2 T/L","지중송전 피뢰기 열화진단","154kV 고령-논공#2T/L C/H 피뢰기 열화진단","2020-09-26 14:00","2020-09-26 18:00","2020-09-26 14:00","2020-09-26 18:00","연속"]
[437,"대구","달성","고령S/S 154kV #65 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경","2020-09-18 18:00","2020-09-19 18:00","취소","취소","연속"]
[438,"대구","달성","달성상인#1 T/L","달성,상인S/S 달성-상인#1T/L 보통점검","달성,상인S/S 달성-상인#1T/L 보통점검","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[439,"대구","달성","대구청도#1 T/L","154kV 대구-청도T/L 용량증대 전선교체공사","대구-청도T/L 용량증대 전선교체 교체구간:대구S/T ~ 청도S/T","2020-09-20 07:00","2020-09-27 18:00","2020-09-20 07:00","2020-09-27 18:00","연속"]
[440,"대구","달성","대구청도#2 T/L","154kV 대구-청도T/L 용량증대 전선교체공사","대구-청도T/L 용량증대 전선교체 교체구간:대구S/T ~ 청도S/T","2020-09-12 07:00","2020-09-19 18:00","2020-09-12 07:00","2020-09-19 18:00","연속"]
[441,"대구","직할","범물남대구#1 T/L","남대구 전자변교체, GIS 보통점검","남대구 전자변교체, GIS 보통점검","2020-09-25 09:30","2020-09-25 18:00","2020-09-25 09:30","2020-09-25 18:00","연속"]
[442,"대구","직할","범물남대구#2 T/L","남대구 전자변교체, GIS 보통점검","남대구 전자변교체, GIS 보통점검","2020-09-28 09:30","2020-09-28 18:00","2020-09-28 09:30","2020-09-28 18:00","연속"]
[443,"대구","칠곡","서대구남구미#1 T/L","154kV남구미-농소T/L No.20 안전이격 확보공사","154kV남구미-농소T/L No.20 안전이격 확보공사","2020-09-04 07:00","2020-10-20 18:00","2020-09-04 07:00","2020-10-20 18:00","연속"]
[444,"대구","칠곡","남구미농소#1 T/L","154kV남구미-농소T/L No.20 안전이격 확보공사","154kV남구미-농소T/L No.20 안전이격 확보공사","2020-09-04 07:00","2020-10-20 18:00","2020-09-04 07:00","2020-10-20 18:00","연속"]
[445,"대구","포항","신포항상정#2 T/L","신포항S/S 154kV 옥외철구 설비 GIS화 공사","- 현대제철,상정#1,2T/L 병가철탑~ST철구간 경간 변경(OPGW 포함) - 상정#2T/L 계탑, BEAM 대체 - 신포항,상정S/S 송전선로 보호반 대체 - 상정#1,2T/L EBA 애관설치, AC내전압 시험, 인출측 분기선 EBA 접속 - 현대제철T/L 인출측 분기선 GIS 부싱접속 - 옥외철구 -> GIS 부하이양 (인출측 분기선 철거 및","2020-09-28 08:00","2020-10-07 18:00","2020-09-28 08:00","2020-10-07 18:00","연속"]
[446,"대구","포항","신포항상정#1 T/L","신포항S/S 154kV 옥외철구 설비 GIS화 공사","- 현대제철,상정#1,2T/L 병가철탑~ST철구간 경간 변경(OPGW 포함) - 상정#2T/L 계탑, BEAM 대체 - 신포항,상정S/S 송전선로 보호반 대체 - 상정#1,2T/L EBA 애관설치, AC내전압 시험, 인출측 분기선 EBA 접속 - 현대제철T/L 인출측 분기선 GIS 부싱접속 - 옥외철구 -> GIS 부하이양 (인출측 분기선 철거 및","2020-09-28 08:00","2020-10-07 18:00","2020-09-28 08:00","2020-10-07 18:00","연속"]
[447,"대구","포항","신포항영일#1 T/L","'20-21년도 포항전력지사 가공송전 정비회사 총액공사","154kV 신포항-영일#1 T/L 피뢰기 설치 : No.12~18","2020-09-30 08:00","2020-10-01 18:00","2020-09-30 08:00","2020-10-01 18:00","연속"]
[448,"경북","구미","남인동인동#2 T/L","남인동S/S 170kV GIS교체공사[1차수]","- #2BUS 24H 무부하가압용 TEST선로 - 서대구-남인동#2T/L(647), #2M.Tr(6233) GIS교체","2020-09-08 18:00","2020-09-09 18:00","2020-09-08 18:00","2020-09-09 18:00","연속"]
[449,"경북","구미","남인동인동#2 T/L","남인동S/S 170kV GIS교체공사[1차수]","- #1BUS 24H 무부하가압용 TEST선로 - 서대구-남인동#2T/L(647), #2M.Tr(6233) GIS교체","2020-09-18 18:00","2020-09-21 09:00","2020-09-18 18:00","2020-09-21 09:00","연속"]
[450,"경북","구미","점촌동상주개폐소#2 T/L","154kV 동상주-점촌T/L 지장이설공사","- 154kV 동상주-점촌T/L No.8 C/H 조립","2020-09-21 08:00","2020-09-23 18:00","2020-09-21 08:00","2020-09-23 18:00","연속"]
[451,"경북","구미","점촌동상주개폐소#1 T/L","154kV 동상주-점촌T/L 지장이설공사","- 154kV 동상주-점촌T/L No.8 C/H 조립","2020-09-21 08:00","2020-09-23 18:00","2020-09-21 08:00","2020-09-23 18:00","연속"]
[452,"경북","영주","문경단양 T/L","영주전력지사 '96년 상반기 이전 국산애자 교체공사","154kV 영주-봉화T/L 등 6개T/L 애자 2218개 , 애자련 227련 교체","2020-09-20 07:00","2020-09-20 18:00","취소","취소","연속"]
[453,"경북","영주","봉화현종산풍력 T/L","2020-21년 영주전력지사 변전정비회사 총액공사","- 617 차단기 전자변 교체 및 조작시험","2020-09-28 09:00","2020-09-28 18:00","2020-09-28 09:00","2020-09-28 18:00","연속"]
[454,"경북","영주","봉화울진 T/L","2020-21년 영주전력지사 변전정비회사 총액공사","- 627 차단기 전자변 교체 및 조작시험","2020-09-21 09:00","2020-09-21 18:00","2020-09-21 09:00","2020-09-21 18:00","연속"]
[455,"경북","영주","신영주안동#1 T/L","영주전력지사 '96년 상반기 이전 국산애자 교체공사","154kV 영주-봉화T/L 등 6개T/L 애자 2218개 , 애자련 227련 교체","2020-09-16 07:00","2020-09-16 18:00","취소","취소","연속"]
[456,"경북","영주","신영주안동#2 T/L","영주전력지사 '96년 상반기 이전 국산애자 교체공사","154kV 영주-봉화T/L 등 6개T/L 애자 2218개 , 애자련 227련 교체","2020-09-17 07:00","2020-09-18 18:00","취소","취소","연속"]
[457,"경북","영주","점촌단양 T/L","영주전력지사 '96년 상반기 이전 국산애자 교체공사","154kV 영주-봉화T/L 등 6개T/L 애자 2218개 , 애자련 227련 교체","2020-09-12 07:00","2020-09-13 18:00","취소","취소","연속"]
[458,"경북","영주","점촌문경 T/L","2020-21년 영주전력지사 변전정비회사 총액공사","- 점촌S/S 657 차단기 보통점검 및 전자변 교체, PT 보통점검 - 문경S/S 617 차단기 보통점검, LA 보통점검","2020-09-19 09:00","2020-09-19 18:00","취소","취소","연속"]
[459,"경북","직할","울진삼척GP#1 T/L","20~21년 경북본부 직할 변전정비회사 총액공사","울진S/S 154kV 울진-삼척GP #1 T/L GIS 보통점검, CVT 초기점검","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[460,"경북","직할","울진삼척GP#2 T/L","20~21년 경북본부 직할 변전정비회사 총액공사","울진S/S 154kV 울진-삼척GP #2 T/L GIS 보통점검, CVT 초기점검","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[461,"경북","직할","현종산풍력평해#1 T/L","154kV 평해S/S 옥외철구설비 현대화 공사","170kV GIS 기초부지 정비","2020-09-25 09:00","2020-09-25 18:00","2020-09-25 09:00","2020-09-25 18:00","연속"]
[462,"경북","직할","현종산풍력평해#2 T/L","154kV 평해S/S 옥외철구설비 현대화 공사","170kV GIS 기초부지 정비","2020-09-24 09:00","2020-09-24 18:00","2020-09-24 09:00","2020-09-24 18:00","연속"]
[463,"부산울산","동부산","수영정보#1 T/L","수영S/S 154kV GIS 차단기 동작시험","1.수영S/S 154kV GIS 차단기 동작시험(수영-정보#1/L) 2.정보S/S 154kV GIS 차단기 동작시험","2020-09-19 09:30","2020-09-19 17:00","2020-09-19 09:30","2020-09-19 17:00","연속"]
[464,"부산울산","북부산","매리김해#2 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #2T/L 임시선로 구성(4회선, 호포-매리#2 포함) ○ 가철탑 24-1, 1-1호 설치","2020-09-19 07:00","2020-09-20 18:00","취소","취소","연속"]
[465,"부산울산","북부산","호포매리#2 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #2T/L 임시선로 구성(4회선, 매리-김해#2 포함) ○ 가철탑 24-1, 1-1호 설치","2020-09-19 07:00","2020-09-20 18:00","취소","취소","연속"]
[466,"부산울산","북부산","호포매리#1 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #1T/L 임시선로 구성(4회선, 매리-김해#1 포함)","2020-09-26 07:00","2020-09-27 18:00","취소","취소","연속"]
[467,"부산울산","북부산","매리김해#1 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #1T/L 임시선로 구성(4회선, 호포-매리#1 포함)","2020-09-26 07:00","2020-09-27 18:00","취소","취소","연속"]
[468,"부산울산","북부산","물금삼랑진PP#1 T/L","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사(41경간, 12.415km)","2020-09-10 07:00","2020-09-29 18:00","2020-09-10 07:00","2020-09-29 18:00","연속"]
[469,"부산울산","북부산","물금삼랑진PP#2 T/L","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사 작업자 안전확보","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사(41경간, 12.415km) 1~15호 병가구간 작업자 안전확보","2020-09-10 07:00","2020-09-20 18:00","2020-09-10 07:00","2020-09-20 18:00","연속"]
[470,"부산울산","북부산","북부산물금 T/L","20-21 북부산전력지사 변전 총액공사","북부산S/S 154kV 북부산-물금T/L GIS 하자점검","2020-09-28 10:00","2020-09-28 18:00","2020-09-28 10:00","2020-09-28 18:00","연속"]
[471,"부산울산","북부산","양산산막#1 T/L","산막S/S 옥상방수공사(안전이격)","산막S/S 옥상방수공사 - 안전이격확보 : 154kV 양산-산막#1T/L 휴전 - 공사감독 : 토건운영부 김태완","2020-09-08 09:00","2020-09-08 18:00","2020-09-08 09:00","2020-09-08 18:00","연속"]
[472,"부산울산","북부산","양산산막#1 T/L","2020 북부산전력지사 154kV GIS 정밀점검","산막S/S 154kV #4M.Tr 1차 GIS(6433) 정밀점검 - 시험가압 (시험가압선로 : 양산-산막#1T/L)","2020-09-27 17:00","2020-09-27 18:00","2020-09-27 17:00","2020-09-27 18:00","연속"]
[473,"부산울산","북부산","주촌삼계#1 T/L","2020 북부산전력지사 154kV GIS 정밀점검","삼계S/S 154kV 6100 BUS-TIE GIS 정밀점검 - 시험가압 (시험가압선로 : 주촌-삼계#1T/L)","2020-09-25 17:00","2020-09-25 18:00","2020-09-25 17:00","2020-09-25 18:00","연속"]
[474,"부산울산","북부산","삼계S/S 154kV #65 BUS","2020 북부산전력지사 154kV GIS 정밀점검","삼계S/S 154kV 6100 BUS-TIE GIS 정밀점검 - 154kV #65BUS 휴전","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[475,"부산울산","서부산","서부산S/S 154kV #60 BUS","서부산S/S 154kV #1 S/T GIS 정밀점검","서부산S/S 154kV #1 S/T GIS 정밀점검 CB, 1DS 정밀점검 시험가압","2020-09-08 09:00","2020-09-09 18:00","2020-09-08 09:00","2020-09-09 18:00","연속"]
[476,"부산울산","서부산","서부산S/S 154kV #61 BUS","서부산S/S 154kV 서부산-신평#1T/L GIS 정밀점검","서부산S/S 154kV 서부산-신평#1T/L GIS 정밀점검 CB, 1DS 정밀점검","2020-09-21 09:00","2020-09-22 18:00","2020-09-21 09:00","2020-09-22 18:00","연속"]
[477,"부산울산","서부산","서부산S/S 154kV #66 BUS","서부산S/S 154kV 서부산-신평#1T/L GIS 정밀점검","서부산S/S 154kV 서부산-신평#1T/L GIS 정밀점검 2DS 정밀점검","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[478,"부산울산","서부산","서부산S/S 154kV #65 BUS","서부산S/S 154kV #1 S/T GIS 정밀점검","서부산S/S 154kV #1 S/T GIS 정밀점검 2DS 정밀점검 시험가압","2020-09-10 09:00","2020-09-10 18:00","2020-09-10 09:00","2020-09-10 18:00","연속"]
[479,"부산울산","서부산","서부산S/S 154kV #61 BUS","서부산S/S 154kV 서부산-신평#2T/L GIS 정밀점검","서부산S/S 154kV 서부산-신평#2T/L GIS 정밀점검 CB, 1DS 정밀점검","2020-09-24 09:00","2020-09-25 18:00","2020-09-24 09:00","2020-09-25 18:00","연속"]
[480,"부산울산","서부산","서부산S/S 154kV #1 S/T CB 687","서부산S/S 154kV #1 S/T GIS 정밀점검","서부산S/S 154kV #1 S/T GIS 정밀점검 CB, 1DS, 2DS 정밀점검","2020-09-08 09:00","2020-09-10 18:00","2020-09-08 09:00","2020-09-10 18:00","연속"]
[481,"부산울산","서부산","서부산S/S 154kV #66 BUS","서부산S/S 154kV 서부산-신평#2T/L GIS 정밀점검","서부산S/S 154kV 서부산-신평#2T/L GIS 정밀점검 2DS 정밀점검 시험가압","2020-09-26 09:00","2020-09-26 18:00","2020-09-26 09:00","2020-09-26 18:00","연속"]
[482,"부산울산","서부산","다대장림 T/L","154kV 다대-신평T/L 등 3개T/L 지장이설공사","[을숙도대교~장림고개 간 지하차도 건설공사] 지장 지중송전설비 이설 - 케이블 포설 : 4구간, 접속 : IJ(9상), NJ(12상)","2020-09-21 09:00","2020-10-02 18:00","2020-09-21 09:00","2020-10-02 18:00","연속"]
[483,"부산울산","울산","신울산명례#2 T/L","신울산S/S 154kV 덕하전철 신규수용공사","신규고객선로 GCB 2CB(6R7,6S7 신설분) 24시간 시험가압","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]
[484,"부산울산","울산","온산처용#1 T/L","선도전기 송전선로 유사고장 방지 성능개선","- 선도전기 송전선로 보호계전기 성능개선(제작사 입회) - 43RC 상태의 간헐적 불필요한 복귀현상 개선 등 펌웨어 성능개선","2020-09-23 09:00","2020-09-23 18:00","2020-09-23 09:00","2020-09-23 18:00","연속"]
[485,"부산울산","울산","울산T/P 154kV #65 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 대체 및 증설공사","1. 6C7(울산피피T/L) GIS 증설 - 상체크(보호제어과) 2. 시험가압일정 / 대상/가압경로 ㅇ 9.02 10:00~ 9.02 10:30(0.5h) 65BUS, 6C2(투입) / 울산-울산TP #2","2020-09-02 10:00","2020-09-02 10:30","2020-09-02 10:00","2020-09-02 10:30","연속"]
[486,"부산울산","울산","울산T/P 154kV #60 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 대체 및 증설공사","1. 6C7(울산피피T/L) GIS 증설 2. 시험가압일정 / 대상/가압경로 ㅇ 9.01 10:00~ 9.02 10:00(24h) 60BUS, 6C1(투입) / 울산-울산TP #2","2020-09-01 10:00","2020-09-02 10:00","2020-09-01 10:00","2020-09-02 10:00","연속"]
[487,"부산울산","울산","울산울산TP#2 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 대체 및 증설공사","1. 6C7(울산피피T/L) GIS 증설 2. 시험가압일정 / 대상/가압경로 ㅇ 9.01 10:00~ 9.02 10:00(24h) 60BUS, 6C1(투입) / 울산-울산TP #2 ㅇ 9.02 10:00~ 9.02 10:30(0.5h) 65BUS, 6C2(투입) / 울산-울산TP #2 (상체크)","2020-09-01 10:00","2020-09-02 10:30","2020-09-01 10:00","2020-09-02 10:30","연속"]
[488,"부산울산","울산","울산울산TP#2 T/L","2020년 울산S/S 154kV SW증설공사","- 울산S/S 154kV SW증설 6B7, 6C7GIS 최초가압용 시험가압선로(24H) - CB, #2DS, #6DS, C/H Chamber, 상부BUS","2020-09-19 09:30","2020-09-20 09:30","2020-09-19 09:30","2020-09-20 09:30","연속"]
[489,"부산울산","울산","울주직동#1 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 직동-반천#2T/L 휴전관련)","2020-09-25 09:00","2020-09-28 18:00","2020-09-25 09:00","2020-09-28 18:00","매일"]
[490,"부산울산","울산","울주직동#2 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 직동-반천#1T/L 휴전관련)","2020-09-22 09:00","2020-09-23 18:00","2020-09-22 09:00","2020-09-23 18:00","연속"]
[491,"부산울산","울산","웅촌서창#1 T/L","2020-21년 울산전력지사 변전협력회사 총액공사","-송전선로 보호반 대체","2020-09-22 09:00","2020-09-24 18:00","2020-09-22 09:00","2020-09-24 18:00","연속"]
[492,"부산울산","울산","효문방어진 T/L","2020-21년 울산전력지사 변전협력회사 총액공사","- #2-1 VCB 대체 관련 안전이격","2020-09-14 09:00","2020-09-18 18:00","2020-09-14 09:00","2020-09-18 18:00","매일"]
[493,"부산울산","직할","정보대연 T/L","2020년 직할 변전정비회사 총액공사","대연S/S 정보-대연T/L PNL 대체","2020-09-26 09:00","2020-09-28 18:00","2020-09-26 09:00","2020-09-28 18:00","연속"]
[494,"부산울산","직할","양정범천 T/L","범천S/S 154kV 장기사용 GIS 대체공사(3차공정)","1.170kV 50kA 2,000A GIS(T/L) × 4CCT 대체 2.170kV 50kA 1,250A GIS(T/R) × 2CCT 대체 3.170kV 50kA 2,000A GIS(B/T) × 1CCT 대체 4.170kV 50kA PT&ES × 1CCT 대체 5.기타 부대공사 × 1식","2020-09-14 07:30","2020-10-16 18:00","2020-09-14 07:30","2020-10-16 18:00","연속"]
[495,"경남","직할","신월삼정#1 T/L","삼정S/S GIS화 154kV 신월-삼정#1T/L 인출변경","삼정S/S GIS화 154kV 신월-삼정#1T/L 인출변경, (구)삼정S/S에서 (신)삼정SA변전소","2020-09-08 08:00","2020-10-09 17:30","2020-09-08 08:00","2020-10-09 17:30","연속"]
[496,"경남","직할","신김해주촌#1 T/L","신김해S/S 154kV 장기사용GIS 교체공사(1차)","신김해S/S 154kV 장기사용GIS 교체공사(1차) 대상 : 신김해-지사#2, 신김해-주촌#1T/L GIS","2020-09-09 08:00","2020-09-29 18:00","2020-09-09 08:00","2020-09-29 18:00","연속"]
[497,"경남","직할","신김해지사#2 T/L","신김해S/S 154kV 장기사용GIS 교체공사(1차)","신김해S/S 154kV 장기사용GIS 교체공사(1차) 대상 : 신김해-지사#2, 신김해-주촌#1T/L GIS","2020-09-09 08:00","2020-09-29 18:00","2020-09-09 08:00","2020-09-29 18:00","연속"]
[498,"경남","직할","신월동읍#2 T/L","신월S/S 154kV 신월-동읍#2T/L GIS 전자변 교체","신월S/S 154kV 신월-동읍#2T/L GIS 전자변 교체","2020-09-04 09:30","2020-09-04 17:30","2020-09-04 09:30","2020-09-04 17:30","연속"]
[499,"경남","진주","하동개양#1 T/L","154kV 하동-개양#1,2T/L 송전선로 정밀점검","154kV 하동-개양#1,2T/L 송전선로 정밀점검","2020-09-05 08:30","2020-09-06 17:00","2020-09-05 08:30","2020-09-06 17:00","매일"]
[500,"경남","진주","하동개양#2 T/L","154kV 하동-개양#1,2T/L 송전선로 정밀점검","154kV 하동-개양#1,2T/L 송전선로 정밀점검","2020-09-05 08:30","2020-09-06 17:00","2020-09-05 08:30","2020-09-06 17:00","매일"]
[501,"경남","진주","의령산청 T/L","의령S/S 의령-산청T/L GIS 조작시험","의령S/S 의령-산청T/L GIS 조작시험","2020-09-29 10:00","2020-09-29 14:00","2020-09-29 10:00","2020-09-29 14:00","연속"]
[502,"경남","진주","하동S/S 154kV CB 6100","하동S/S 154kV #1BUS TIE GIS 조작시험","하동S/S 154kV #1BUS TIE GIS 조작시험","2020-09-25 10:00","2020-09-25 14:00","2020-09-25 10:00","2020-09-25 14:00","연속"]
[503,"경남","진주","산청함양 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 공사 - (신)변전소 가압시행 1. 산청함양T/L 휴전 2. 산청함양T/L 보호계전기 이설작업 3. 산청함양T/L 인출변경","2020-09-19 08:00","2020-09-20 19:00","2020-09-19 08:00","2020-09-20 19:00","연속"]
[504,"경남","진주","함양거창#1 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 공사 - (신)변전소 가압시행 1. 함양-거창#1T/L 휴전 2. 함양-거창#1T/L 보호계전기 이설작업 3. 함양S/S (신)변전소 시험가압 시행","2020-09-16 07:30","2020-09-18 19:00","2020-09-16 07:30","2020-09-18 19:00","연속"]
[505,"경남","진주","함양거창#2 T/L","154kV 거창-합천T/L 지장이설관련 OPGW 교체공사","OPGW 100SQ, 48C 교체: 3.689km","2020-09-14 06:00","2020-09-15 19:00","2020-09-14 06:00","2020-09-15 19:00","매일"]
[506,"경남","진주","합천수력#1 T/L","154kV 쌍림-합천#2T/L 휴전작업 안전거리확보","154kV 쌍림-합천#2T/L 불량애자 의심개소 사선확인 및 교체작업 안전거리 확보","2020-09-22 15:30","2020-09-22 18:00","2020-09-22 15:30","2020-09-22 18:00","연속"]
[507,"경남","진주","쌍림합천#1 T/L","154kV 쌍림-합천#1T/L 불량애자 의심개소 사선확인 및 교체","154kV 쌍림-합천#1T/L 불량애자 의심개소 사선확인 및 교체","2020-09-22 12:30","2020-09-22 15:00","2020-09-22 12:30","2020-09-22 15:00","연속"]
[508,"경남","진주","합천수력#2 T/L","154kV 쌍림-합천#1T/L 휴전작업 안전거리확보","154kV 쌍림-합천#1T/L 불량애자 의심개소 사선확인 및 교체작업 안전거리 확보","2020-09-22 12:30","2020-09-22 15:00","2020-09-22 12:30","2020-09-22 15:00","연속"]
[509,"경남","진주","쌍림합천#2 T/L","154kV 쌍림-합천#2T/L 불량애자 의심개소 사선확인 및 교체","154kV 쌍림-합천#2T/L 불량애자 의심개소 사선확인 및 교체","2020-09-22 15:30","2020-09-22 18:00","2020-09-22 15:30","2020-09-22 18:00","연속"]
[510,"경남","통영","삼천포사천#2 T/L","삼천포S/S 170kV (신)B/T 시험가압","삼천포S/S 170kV 장기사용 GIS 대체공사(BUS TIE) - 삼천포S/S (신)BUS TIE 시험가압(2BUS)","2020-09-26 14:00","2020-09-28 09:00","2020-09-26 14:00","2020-09-28 09:00","연속"]
[511,"경남","통영","삼천포S/S 154kV CB 6100","삼천포S/S 170kV 장기사용 GIS 대체공사(1차공정)","삼천포S/S 170kV 장기사용 GIS 대체공사(BUS TIE) - 1차공정 : 170kV (신)B/T 설치","2020-09-14 09:30","2020-09-28 17:00","2020-09-14 09:30","2020-09-28 17:00","연속"]
[512,"경남","통영","삼천포사천#1 T/L","삼천포S/S 170kV (신)B/T 시험가압","삼천포S/S 170kV 장기사용 GIS 대체공사(BUS TIE) - 1차공정 : 170kV (신)B/T 설치","2020-09-19 14:00","2020-09-21 09:00","2020-09-19 14:00","2020-09-21 09:00","연속"]
[513,"경남","통영","신고성거제#2 T/L","154kV 신고성-거제#2T/L 폴리머애자 교체","154kV 신고성-거제#2T/L 폴리머애자 교체(161~183호)","2020-09-12 08:00","2020-09-13 18:00","2020-09-12 08:00","2020-09-13 18:00","매일"]
[514,"경남","통영","신고성거제#2 T/L","154kV 신고성-거제#2T/L 폴리머애자 교체","154kV 신고성-거제#2T/L 폴리머애자 교체(161~183호)","2020-09-19 08:00","2020-09-20 18:00","2020-09-19 08:00","2020-09-20 18:00","매일"]
[515,"경남","통영","신고성거제#2 T/L","154kV 신고성-거제#2T/L SB댐퍼 교체","154kV 신고성-거제#2T/L SB댐퍼 교체(145~146, 154~156호)","2020-09-26 08:00","2020-09-27 18:00","2020-09-26 08:00","2020-09-27 18:00","매일"]
[516,"경남","통영","통영거제#2 T/L","통영S/S 154kV 통영-거제#2T/L ES 투입불량 보수","1. 통영S/S 154kV 통영-거제#2T/L ES 투입불량 보수","2020-09-05 09:30","2020-09-05 18:00","2020-09-05 09:30","2020-09-05 18:00","연속"]
[517,"경남","함안","가야사봉#2 T/L","154kV 가야-사봉#1,2T/L 불량애자 교체 공사","154kV 가야-사봉#1 T/L 4,6,11,12,26호 7련 70개 교체 안전확보차 및 154kV 가야-사봉#2 T/L S/T 9련 84개 교체","2020-09-12 08:00","2020-09-14 18:00","2020-09-12 08:00","2020-09-14 18:00","연속"]
[518,"경남","함안","가야사봉#1 T/L","154kV 가야-사봉#1,#2 T/L 불량애자 교체 공사","154kV 가야-사봉#1 T/L 4,6,11,12,26호 7련 70개 교체","2020-09-12 08:00","2020-09-14 18:00","2020-09-12 08:00","2020-09-14 18:00","매일"]
[519,"경남","함안","진영수산#1 T/L","154kV 진영-수산#1T/L 불량애자교체","154kV 진영-수산#1T/L 29,34,38호 6련 56개 교체","2020-09-10 08:00","2020-09-11 18:00","2020-09-10 08:00","2020-09-11 18:00","매일"]
[520,"경남","함안","신마산칠서#1 T/L","154kV 신마산-칠서T/L 지장송전선로 이설공사(요청자시행)","- 43~45호 구간 임시선로 구성","2020-09-23 07:00","2020-09-27 18:00","2020-09-23 07:00","2020-09-27 18:00","연속"]
[521,"경남","함안","신마산칠서#2 T/L","154kV 신마산-칠서T/L 지장송전선로 이설공사(요청자시행)","- 43~45호 구간 임시선로 구성","2020-09-18 07:00","2020-09-22 18:00","2020-09-18 07:00","2020-09-22 18:00","연속"]
[522,"경남","함안","진영수산#2 T/L","진영S/S 154kV 진영-수산#2T/L GIS 조작시험","진영S/S 154kV 진영-수산#2T/L GIS 조작시험","2020-09-28 09:30","2020-09-28 13:30","2020-09-28 09:30","2020-09-28 13:30","연속"]
[523,"경남","함안","창녕초동#2 T/L","154kV 창녕-초동#2T/L 불량애자교체공사","154kV 창녕-초동#2T/L 10호 불량애자교체","2020-09-11 08:00","2020-09-11 18:00","2020-09-11 08:00","2020-09-11 18:00","연속"]
[524,"남서울","영등포","가양등촌#2 T/L","154kV 가양S/S 인출전력구 케이블 선종교체공사","가양S/S 인출전력구 케이블 선종교체공사 구간 : 가양S/S EBG ~ J/B#38(OF→XLPE)","2020-09-01 09:00","2020-10-26 18:00","2020-09-01 09:00","2020-10-26 18:00","연속"]
[525,"전북","김제","신김제S/S 154kV SEC CB 65660","신김제S/S 노후 170GIS 교체","장기사용 노후 170GIS 교체공사 ","2020-09-14 18:00","2020-09-23 18:00","2020-09-14 18:00","2020-09-23 18:00","연속"]