{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["765송부","345송부","154송부"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":12,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"765송부","index":0,"n_rows":20,"n_cols":11,"rows_kept":20,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 10월 휴전계획서"]
["765kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"경기북부","구리","신가평S/S #2 M.Tr","'20-21년 구리전력지사 변전정비회사 총액공사","장기사용 배전반 교체공사 - 345kV #75BAY B/F반 교체","2020-10-15 09:00","2020-10-23 18:00","2020-10-15 09:00","2020-10-23 18:00","연속"]
[2,"경기","성남","신안성S/S 765kV CB 8772","신안성 765kV GIS 보통점검","신안성 765kV GIS 보통점검","2020-10-26 09:00","2020-10-27 18:00","취소","취소","연속"]
[3,"경기","성남","신안성S/S 765kV CB 8700","신안성 765kV GIS 보통점검","신안성 765kV GIS 보통점검","2020-10-28 09:00","2020-10-29 18:00","취소","취소","연속"]
[4,"경기","성남","신안성S/S #3 M.Tr A-1","신안성변전소 765kV 변압기 정밀점검","변압기정밀점검","2020-10-12 09:00","2020-12-04 18:00","2020-10-12 09:00","2020-12-04 18:00","연속"]
[5,"충북","직할","신중부S/S 765kV CB 8671","765kV GIS 8671CB 하자보수","8671CB B상 개폐타임 기준치 미충족으로 동작롯트 조정 시행","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[6,"충북","직할","신중부S/S 765kV CB 8800","765kV GIS 8800CB 하자보수","8800CB 조작함 내부 오일누유 및 8809-4ES C상 DC코일 교체","2020-10-12 09:00","2020-10-12 18:00","2020-10-12 09:00","2020-10-12 18:00","연속"]
[7,"대전충남","서산","당진T/P 765kV CB 8700","20년 서산P/O 765kV GIS 정밀점검공사","- 765kV GIS 정밀점검(8772,8702,8762) - 7호기 O/H : 10/12 ~ 11/27 예정","2020-10-19 10:00","2020-10-30 18:00","2020-10-19 10:00","2020-10-30 18:00","연속"]
[8,"대전충남","서산","당진T/P 765kV CB 8772","20년 서산P/O 765kV GIS 정밀점검공사","- 765kV GIS 정밀점검(8772,8702,8762) - 7호기 O/H : 10/12 ~ 11/27 예정","2020-10-19 10:00","2020-10-30 18:00","2020-10-19 10:00","2020-10-30 18:00","연속"]
[9,"대전충남","서산","당진T/P 765kV CB 8372","20년 서산P/O 765kV GIS 정밀점검공사","- 765kV GIS 정밀점검(8372,8302,8362) - 3호기 O/H : 9/11 ~ 12/10 예정","2020-10-05 10:00","2020-10-16 18:00","2020-10-05 10:00","2020-10-16 18:00","연속"]
[10,"대전충남","서산","당진T/P 765kV CB 8300","20년 서산P/O 765kV GIS 정밀점검공사","- 765kV GIS 정밀점검(8372,8302,8362) - 3호기 O/H : 9/11 ~ 12/10 예정","2020-10-05 10:00","2020-10-16 18:00","2020-10-05 10:00","2020-10-16 18:00","연속"]
[11,"대전충남","서산","신서산당진TP#2 T/L","20년 서산P/O 변전정비 총액공사","신서산-당진화력#2T/L 보호반 성능개선","2020-10-22 10:00","2020-10-22 18:00","취소","취소","연속"]
[12,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7177 - 2시간)","2020-10-16 16:00","2020-10-16 18:00","2020-10-16 16:00","2020-10-16 18:00","연속"]
[13,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7A71 - 2시간)","2020-10-09 16:00","2020-10-09 18:00","2020-10-09 16:00","2020-10-09 18:00","연속"]
[14,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7872 - 2시간)","2020-10-23 16:00","2020-10-23 18:00","2020-10-23 16:00","2020-10-23 18:00","연속"]
[15,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7800 - 2시간)","2020-10-30 16:00","2020-10-30 18:00","2020-10-30 16:00","2020-10-30 18:00","연속"]
[16,"부산울산","동부산","신고리N/P #4호기 주변압기 CB (8300, 8372)","신고리4호기 1차 계획예방정비 * 조작차단기 : 8300, 8372","주변압기 점검","2020-10-30 11:00","2020-12-18 15:00","2020-10-30 11:00","2020-12-18 15:00","연속"]

{"sheet":"345송부","index":1,"n_rows":362,"n_cols":11,"rows_kept":362,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 10월 휴전계획서"]
["345kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","성동","성동S/S #1 M.Tr","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020-10-05 09:30","2020-10-14 18:00","취소","취소","연속"]
[2,"서울","성동","성동S/S #4 M.Tr","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020년 성동P/O 345kV M.Tr 및 OLTC 정밀점검공사","2020-10-15 09:30","2020-10-21 18:00","취소","취소","연속"]
[3,"남서울","강남","신양재S/S #1 M.Tr","2020년 강남P/O 345kV 주변압기 정밀점검","- 신양재S/S #1M.Tr 정밀점검","2020-10-12 09:00","2020-10-30 18:00","2020-10-12 09:00","2020-10-30 18:00","연속"]
[4,"남서울","강남","신양재S/S #3 M.Tr","362kV, 170kV GIS 개폐타임 측정-변전협력","- 신양재S/S #3M.Tr 1,2차 GIS 개폐타임 측정 - 362kV 7300 GIS 개폐타임 측정","2020-10-07 10:00","2020-10-07 18:00","2020-10-07 10:00","2020-10-07 18:00","연속"]
[5,"남서울","강남","신양재S/S 345kV CB 7271","362kV GIS 개폐타임 측정-변전협력","- 362kV 7271 GIS 개폐타임 측정","2020-10-08 10:00","2020-10-08 18:00","2020-10-08 10:00","2020-10-08 18:00","연속"]
[6,"남서울","동서울","동서울S/S 345kV CB 7100","SVC 제어시스템 및 리액터 교체 무부하가압","SVC 제어시스템 및 리액터 교체 무부하 가압","2020-10-22 10:00","2020-10-23 10:00","2020-10-22 10:00","2020-10-23 10:00","연속"]
[7,"남서울","동서울","동서울S/S 345kV CB 7500","SVC 제어시스템 및 리액터 교체 무부하가압","SVC 제어시스템 및 리액터 교체 무부하 가압","2020-10-22 10:00","2020-10-23 10:00","2020-10-22 10:00","2020-10-23 10:00","연속"]
[8,"남서울","동서울","동서울S/S 345kV CB 7200","SVC 제어시스템 및 리액터 교체 무부하가압","SVC 제어시스템 및 리액터 교체 무부하 가압","2020-10-22 10:00","2020-10-23 10:00","2020-10-22 10:00","2020-10-23 10:00","연속"]
[9,"남서울","동서울","신용인동서울#1 T/L","동서울S/S 345kV 노후 주변압기 교체공사","○ 345kV M.Tr 7대 교체 ○ 기타 부대작업 1식","2020-10-27T13:00:00","2020-10-28T13:00:00","2020-10-27 13:00","2020-10-28 13:00","연속"]
[10,"남서울","동서울","동서울S/S 345kV #76 BUS","동서울S/S 345kV 노후 주변압기 교체공사","○ 345kV M.Tr 7대 교체 ○ 기타 부대작업 1식","2020-10-27 13:00","2020-10-28 13:00","2020-10-27 13:00","2020-10-28 13:00","연속"]
[11,"남서울","동서울","신성남동서울#2 T/L","20~21년 동서울전력지사 가공송전정비회사 총액공사","철탑 추락방지시설 설치공사","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[12,"남서울","동서울","동서울S/S #1 M.Tr","동서울S/S 345kV 노후 주변압기 교체공사","○ 345kV M.Tr 7대 교체 ○ 기타 부대작업 1식","2020-10-12 09:00","2020-10-30 18:00","2020-10-12 09:00","2020-10-30 18:00","연속"]
[13,"남서울","동서울","동서울미금#1 T/L","154kV 동서울-강동T/L 등 5개 T/L 지중화(이설)공사","345KV 동서울-미금T/L 가철탑 연선 및 긴선(이설요청자 한국도로공사 시행)","2020-10-28 08:00","2020-11-16 18:00","취소","취소","연속"]
[14,"남서울","동서울","동서울미금#2 T/L","154kV 동서울-강동T/L 등 5개 T/L 지중화(이설)공사","345KV 동서울-미금T/L 가철탑 연선 및 긴선(이설요청자 한국도로공사 시행)","2020-10-28 09:00","2020-11-16 18:00","취소","취소","연속"]
[15,"남서울","동서울","동서울S/S SVC CB","SVC 제어시스템 및 리액터 교체","SVC 제어시스템 및 리액터 교체","2020-10-13 09:00","2020-10-23 18:00","2020-10-13 09:00","2020-10-23 18:00","연속"]
[16,"남서울","영등포","신광명S/S #2 M.Tr","신광명S/S #2M.Tr 접지발생개소 해소","- 아인(송변)-1203('20.6.25) 관련 접지발생개소 해소 시행","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[17,"남서울","영등포","신광명영등포#2 T/L","신광명S/S 345kV GIS 보통점검(신광명-영등포#2T/L)","- 345kV GIS 보통점검 - SF6 가스 수분 및 SO2 측정 - 차단기 개폐타임 측정 - 절연저항 측정","2020-10-17 14:00","2020-10-17 18:00","취소","취소","연속"]
[18,"남서울","영등포","신광명영등포#1 T/L","신광명S/S 345kV GIS 보통점검(신광명-영등포#1T/L)","- 345kV GIS 보통점검 - SF6 가스 수분 및 SO2 측정 - 차단기 개폐타임 측정 - 절연저항 측정","2020-10-17 09:00","2020-10-17 14:00","취소","취소","연속"]
[19,"남서울","영등포","신광명S/S #1 M.Tr","신광명S/S #1M.Tr 부싱절연유 채유 등 2개 작업","- #1M.Tr B상 1,2차 부싱절연유 채유 - 부싱 절연열화 측정","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[20,"남서울","영등포","신광명S/S #3 M.Tr","신광명S/S #3M.Tr 접지발생개소 해소","- 아인(송변)-1203('20.6.25) 관련 접지발생개소 해소 시행","2020-10-21 09:00","2020-10-22 18:00","2020-10-21 09:00","2020-10-22 18:00","연속"]
[21,"남서울","영등포","서서울신광명#1 T/L","신광명S/S 345kV 송전선로 보호반 교체공사","- 서서울-신광명#1T/L 송전선로 보호반 교체","2020-10-05 09:00","2020-10-08 18:00","취소","취소","연속"]
[22,"남서울","영등포","서서울신광명#2 T/L","신광명S/S 345kV 송전선로 보호반 교체공사","- 서서울-신광명#2T/L 보호반 교체","2020-10-12 09:00","2020-10-16 18:00","취소","취소","연속"]
[23,"남서울","직할","영등포S/S #3 M.Tr","영등포S/S 345kV 주변압기 정밀점검","영등포S/S 345kV 주변압기 정밀점검 상판누유보수","2020-10-19 09:00","2020-11-03 18:00","2020-10-19 09:00","2020-11-03 18:00","연속"]
[24,"남서울","직할","영등포S/S #2 M.Tr","영등포S/S 345kV 주변압기 정밀점검","영등포S/S 345kV 주변압기 정밀점검 상판누유보수","2020-10-05 09:00","2020-10-19 09:00","2020-10-05 09:00","2020-10-19 09:00","연속"]
[25,"남서울","동서울","동서울미금#1 T/L","20~21년 동서울전력지사 가공송전정비회사 총액공사","철탑 추락방지시설 설치공사","2020-10-19T08:00:00","2020-10-19T18:00:00","2020-10-19T08:00:00","2020-10-19T18:00:00","연속"]
[26,"남서울","동서울","동서울미금#2 T/L","20~21년 동서울전력지사 가공송전정비회사 총액공사","철탑 추락방지시설 설치공사","2020-10-19T08:00:00","2020-10-19T18:00:00","2020-10-19T08:00:00","2020-10-19T18:00:00","연속"]
[27,"인천","부평","신경서신인천CC T/L","신경서S/S 345kV 7161DS GIS 내부점검","신경서S/S 345kV 7161DS GIS 내부점검","2020-10-01 09:00","2020-10-02 18:00","2020-10-01 09:00","2020-10-02 18:00","연속"]
[28,"인천","부평","신가좌S/S 345kV #1 BUS","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -7351DS 설치 -#70BUS Main PT 철거 및 설치 -실부하가압 관련 앵글 측정","2020-10-05 09:00","2020-10-18 18:00","2020-10-05 09:00","2020-10-22 09:00","연속"]
[29,"인천","부평","신가좌가정#1 T/L","신가좌S/S 362kV 용량부족 GIS 교체공사","- 휴전사유 : 70BUS 휴전시 신가좌가정#1T/L 무압","2020-10-05 09:00","2020-10-18 18:00","2020-10-05 09:00","2020-10-22 09:00","연속"]
[30,"인천","부평","신경서S/S 345kV CB 7271","2020년 부평전력지사 362kV GIS 정밀점검","신경서인천CC#1T/L 7271 GIS 정밀점검","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[31,"인천","직할","신부평S/S 345kV CB 7271","신부평S/S 서인천CC신부평#2T/L 7271CB 강화조작시험","신부평S/S 서인천CC신부평#2T/L 7271CB 강화조작시험","2020-10-05 09:30","2020-10-05 14:00","2020-10-05 09:30","2020-10-05 14:00","연속"]
[32,"인천","부평","인천C/C #1 Tie-Tr","부평전력지사 345kV 주변압기 정밀점검공사(인천C/C #1Tie-Tr)","인천C/C #1Tie-Tr 정밀점검공사 - 주변압기 정밀점검 - OLTC 정밀점검 - 기계적 보호장치 및 각종 계기류 교체 - #1Tie-Tr 보호반 대체(병행) - 6144 GIS 정밀점검(병행)","2020-10-06 09:00","2020-10-23 18:00","2020-10-06 09:00","2020-10-23 18:00","연속"]
[33,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥#1S/S 154kV 6100 GIS정밀무부하(#1M.Tr휴전)","신시흥#1S/S 154kV 6100 GIS정밀무부하(#1M.Tr휴전)","2020-10-06 16:00","2020-10-06 18:00","취소","취소","연속"]
[34,"인천","시흥","신시흥#2S/S #5 M.Tr","신시흥#2S/S 345kV #5M.Tr 2차 GIS정밀점검","신시흥#2S/S 345kV #5M.Tr 2차 GIS정밀점검","2020-10-07 09:00","2020-10-08 18:00","취소","취소","연속"]
[35,"인천","직할","신부평S/S 345kV #4 Sh.R","2020년도 신부평S/S 362kV GIS 정밀점검공사(7479CB)","신부평S/S 362kV 7479CB 정밀점검","2020-10-12 08:00","2020-10-14 18:00","2020-10-22 08:00","2020-10-24 18:00","연속"]
[36,"인천","부평","포스코CC인천TP#1 T/L","345kV 포스코SY-인천CC T/L 접속함 교체공사","중간접속함 리콜자재(에폭시유니트 불량)로 교체 시행(J/B#2, 3set)","2020-10-12 09:00","2020-10-18 18:00","2020-10-12 09:00","2020-10-18 18:00","연속"]
[37,"인천","시흥","신시흥#2S/S #6 M.Tr","신시흥#2S/S 345kV #6M.Tr 2차 GIS정밀점검","신시흥#2S/S 345kV #6M.Tr 2차 GIS정밀점검","2020-10-12 09:00","2020-10-13 18:00","취소","취소","연속"]
[38,"인천","시흥","신시흥영흥TP#3 T/L","2020-2021년 송전정비회사 총액공사","- 345kV 서서울2-신시흥#2T/L 스페이서간격조정 관련 안전이격거리확보","2020-10-13 08:00","2020-10-13 10:00","취소","취소","연속"]
[39,"인천","부평","서인천C/C #2 Tie-Tr","서인천복합S/Y 345kV #2M.Tr 보통점검 공사","서인천복합S/Y 345kV #2M.Tr 보통점검 공사","2020-10-13 09:00","2020-10-14 18:00","2020-10-13 09:00","2020-10-14 18:00","연속"]
[40,"인천","부평","신경서S/S 345kV CB 7200","2020년 부평전력지사 362kV GIS 정밀점검","신경서인천CC#1T/L-#2M.Tr 1차 7200 GIS 정밀점검","2020-10-13 09:00","2020-10-16 18:00","2020-10-13 09:00","2020-10-16 18:00","연속"]
[41,"인천","직할","신부평S/S 345kV CB 7372","2020년도 신부평S/S 362kV GIS 정밀점검공사(7372CB)","신부평S/S 362kV 7372CB 정밀점검","2020-10-15 08:00","2020-10-17 18:00","2020-10-19 08:00","2020-10-21 18:00","연속"]
[42,"인천","부평","서인천C/C #1 Tie-Tr","서인천복합S/Y 345kV #1M.Tr 부싱유 채유 공사","서인천복합S/Y 345kV #1M.Tr 부싱유 채유 공사","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[43,"인천","시흥","신시흥#2S/S 345kV CB 7671","신시흥#2S/S 345kV 7671 GIS조작시험","신시흥#2S/S 345kV 7671 GIS조작시험","2020-10-15 10:00","2020-10-15 14:00","2020-10-15 10:00","2020-10-15 14:00","연속"]
[44,"인천","시흥","신시흥#2S/S 345kV CB 7600","신시흥#2S/S 345kV 7600 GIS조작시험","신시흥#2S/S 345kV 7600 GIS조작시험","2020-10-15 14:00","2020-10-15 18:00","2020-10-15 14:00","2020-10-15 18:00","연속"]
[45,"인천","부평","신가좌S/S 345kV CB 7600","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -345㎸ #70BUS 무부하 가압용 (24H)","2020-10-17 10:00","2020-10-18 10:00","2020-10-21 10:00","2020-10-22 10:00","연속"]
[46,"인천","직할","신부평S/S 345kV CB 7272","2020년도 신부평S/S 362kV GIS 정밀점검공사(7272CB)","신부평S/S 362kV 7272CB 정밀점검","2020-10-19 08:00","2020-10-21 18:00","2020-10-15 08:00","2020-10-17 18:00","연속"]
[47,"인천","부평","서인천C/C #3 Tie-Tr","서인천복합S/Y 345kV #3M.Tr 보통점검 공사","서인천복합S/Y 345kV #3M.Tr 보통점검 공사","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[48,"인천","부평","신가좌S/S 345kV #2 BUS","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -7352DS 설치 -#75BUS Main PT 철거 및 설치 -실부하가압 관련 앵글 측정","2020-10-19 09:00","2020-11-01 18:00","2020-10-23 09:00","2020-11-09 09:00","연속"]
[49,"인천","부평","포스코CC인천TP#2 T/L","345kV 포스코SY-인천CC T/L 접속함 교체공사","중간접속함 리콜자재(에폭시유니트 불량)로 교체 시행(J/B#2, 3set)","2020-10-19 09:00","2020-10-25 18:00","2020-10-19 09:00","2020-10-25 18:00","연속"]
[50,"인천","시흥","신시흥#2S/S #4 M.Tr","신시흥#2S/S 345kV #4M.Tr 보통점검","신시흥#2S/S 345kV #4M.Tr 보통점검","2020-10-19 10:00","2020-10-21 18:00","2020-10-19 10:00","2020-10-21 18:00","연속"]
[51,"인천","부평","신경서S/S 345kV CB 7100","2020년 부평전력지사 362kV GIS 정밀점검","신경서신인천CCT/L-#1M.Tr 1차 7100 GIS 정밀점검","2020-10-20 09:00","2020-10-23 18:00","2020-10-20 09:00","2020-10-23 18:00","연속"]
[52,"인천","직할","신부평S/S 345kV CB 7172","2020년도 신부평S/S 362kV GIS 정밀점검공사(7172CB)","신부평S/S 362kV 7172CB 정밀점검","2020-10-22 08:00","2020-10-24 18:00","2020-10-12 08:00","2020-10-14 18:00","연속"]
[53,"인천","직할","서인천CC신부평#1 T/L","345kV 서인천CC-신부평 등 2개T/L 절연유 채취밸브 설치공사","[345kV 서인천CC-신부평 등 2개T/L 절연유 채취밸브 설치공사] - 대상선로 : 서인천CC-신부평#1,2,3,4T/L, 신가좌-부개#1,2T/L","2020-10-22 09:00","2020-10-31 18:00","2020-10-22 09:00","2020-10-31 18:00","연속"]
[54,"인천","부평","신경서S/S #3 M.Tr","신경서S/S #3M.Tr 보통점검 공사","신경서S/S #3M.Tr 보통점검 공사","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[55,"인천","부평","인천C/C #2 Tie-Tr","인천복합S/Y #2Tie-Tr 보호반 교체공사","인천복합S/Y #2Tie-Tr 보호반 교체공사","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[56,"인천","부평","신가좌S/S 345kV CB 7600","신가좌S/S 362kV 용량부족 GIS 교체공사","-신가좌S/S 362kV 용량부족 GIS 교체공사 -345㎸ #75BUS 무부하 가압용 (24H)","2020-10-31 10:00","2020-11-01 10:00","2020-11-08 10:00","2020-11-09 10:00","연속"]
[57,"경기북부","고양","신덕은S/S #4 M.Tr","362kV GIS 보통점검 - 변전총액공사","신덕은S/S 7472 GIS 보통점검","2020-10-15 10:00","2020-10-15 18:00","2020-10-15 10:00","2020-10-15 18:00","연속"]
[58,"경기북부","고양","신파주양주#1 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 관형지지물 1기 신설(철탑 조립) ㅇ 기설, 임시철탑 2기 철거 ※ 본 휴전 승인시 해당사업 완료","2020-10-05 07:00","2020-10-07 18:00","2020-10-05 07:00","2020-10-07 18:00","연속"]
[59,"경기북부","고양","신파주양주#1 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 관형지지물 1기 신설(철탑 조립) ㅇ 기설, 임시철탑 2기 철거 ※ 본 휴전 승인시 해당사업 완료","2020-10-12 07:00","2020-10-15 18:00","2020-10-12 07:00","2020-10-15 18:00","연속"]
[60,"경기북부","고양","신파주양주#2 T/L","345kV 신파주-양주T/L No.12 안전이격거리 확보공사","ㅇ 관형지지물 1기 신설(철탑 조립) ㅇ 기설, 임시철탑 2기 철거 ※ 본 휴전 승인시 해당사업 완료","2020-10-08 07:00","2020-10-11 18:00","2020-10-08 07:00","2020-10-11 18:00","연속"]
[61,"경기북부","구리","미금S/S 345kV #1 Sh.R","345kV Sh.R 보통점검","345kV Sh.R 보통점검","2020-10-12 10:00","2020-10-12 18:00","2020-10-12 10:00","2020-10-12 18:00","연속"]
[62,"경기북부","구리","미금성동#1 T/L","미금S/S 362kV GIS PT 대체공사","- 미금-성동#1T/L 인출PT 대체 - #1M.Tr 인출PT 대체 - 기타 부대공사 1식","2020-10-12 09:00","2020-10-21 18:00","2020-10-12 09:00","2020-10-21 18:00","연속"]
[63,"경기북부","구리","미금S/S 345kV #4 Sh.R","345kV Sh.R 보통점검","345kV Sh.R 보통점검","2020-10-14 10:00","2020-10-14 18:00","2020-10-14 10:00","2020-10-14 18:00","연속"]
[64,"경기북부","구리","미금S/S 345kV #5 Sh.R","345kV Sh.R 보통점검","345kV Sh.R 보통점검","2020-10-15 10:00","2020-10-15 18:00","2020-10-15 10:00","2020-10-15 18:00","연속"]
[65,"경기북부","구리","미금S/S STATCOM CB","'20~21년 구리전력지사 변전정비회사 총액공사","미금S/S STATCOM M.Tr, STATCOM AUX M.Tr 보통점검","2020-10-06 10:00","2020-10-08 18:00","2020-10-06 10:00","2020-10-08 18:00","연속"]
[66,"경기북부","구리","미금S/S 345kV #2 Sh.R","345kV Sh.R 보통점검","345kV Sh.R 보통점검","2020-10-13 10:00","2020-10-13 18:00","2020-10-13 10:00","2020-10-13 18:00","연속"]
[67,"경기북부","구리","미금S/S #3 M.Tr","미금 #3M.Tr 부싱절연유 채유","미금 #3M.Tr 부싱절연유 채유","2020-10-08 09:00","2020-10-08 18:00","2020-10-08 09:00","2020-10-08 18:00","연속"]
[68,"경기북부","구리","미금S/S #1 M.Tr","미금S/S 362kV GIS PT 대체공사","- 미금-성동#1T/L 인출PT 대체 - #1M.Tr 인출PT 대체 - 기타 부대공사 1식","2020-10-12 09:00","2020-10-21 18:00","2020-10-12 09:00","2020-10-21 18:00","연속"]
[69,"경기북부","구리","신의정부미금#1 T/L","관내 OPGW 항공장애표시구 설치공사(2020)","- 345kV 신의정부-미금 #1T/L OPGW 1~1.1,62~63 구간 항공장애표시구 7개 설치","2020-10-05 09:00","2020-10-05 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[70,"경기북부","구리","신의정부미금#2 T/L","관내 OPGW 항공장애표시구 설치공사(2020)","- 345kV 신의정부-미금 #2T/L OPGW 1~1.1,62~63 구간 항공장애표시구 8개 설치","2020-10-06 09:00","2020-10-06 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[71,"경기북부","구리","동서울미금#1 T/L","장기사용 성능저하 국산현수애자 교체공사 병가선로","ㅇ 성능저하 애자교체공사 - 대상 : 345kV 신의정부-미금#2T/L","2020-10-06 08:00","2020-10-06 13:00","취소","취소","연속"]
[72,"경기북부","구리","미금S/S 345kV #2 BUS","미금S/S 감시제어설비 교체공사","- 345kV #2 BUS PT용 감시,경보 케이블 교체 (아날로그 → 디지털SA)","2020-10-25 10:00","2020-10-25 15:00","취소","취소","연속"]
[73,"경기북부","구리","미금S/S #2 M.Tr","'20-21년 구리전력지사 변전정비회사 총액공사","장기사용 배전반 교체공사 - 345kV #73BAY B/F반 교체","2020-10-28 09:00","2020-11-03 18:00","2020-10-28 09:00","2020-11-03 18:00","연속"]
[74,"경기북부","구리","미금S/S 345kV #1 BUS","미금S/S 감시제어설비 교체공사","- 345kV #1 BUS PT용 감시,경보 케이블 교체 (아날로그 → 디지털SA)","2020-10-24 10:00","2020-10-24 15:00","취소","취소","연속"]
[75,"경기북부","구리","미금성동#2 T/L","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - 미금S/S 72Bay 관련 차단기 3대 감시제어계측 포인트이관 (→SA) - 72Bay LCP 및 배전반 모자익반 제어케이블 철거 및 재결선 - #3,4Sh.R LCP 및 배전반 모자익반 제어케이블 철거 및 재결선","2020-10-26 09:00","2020-10-30 18:00","취소","취소","연속"]
[76,"경기북부","구리","신가평신의정부#2 T/L","'20-21년 구리전력지사 변전정비회사 총액공사","장기사용 배전반 교체공사 - 345kV #75BAY B/F반 교체","2020-10-15 09:00","2020-10-23 18:00","2020-10-15 09:00","2020-10-23 18:00","연속"]
[77,"경기북부","구리","신포천S/S #2 M.Tr","신포천 #2M.Tr 부싱절연유 채유","신포천 #2M.Tr 부싱절연유 채유","2020-10-13 09:00","2020-10-13 14:00","2020-10-13 09:00","2020-10-13 14:00","연속"]
[78,"경기북부","구리","신포천S/S #3 M.Tr","신포천 #3M.Tr 부싱절연유 채유","신포천 #3M.Tr 부싱절연유 채유","2020-10-13 14:00","2020-10-13 18:00","2020-10-13 14:00","2020-10-13 18:00","연속"]
[79,"경기북부","구리","포천LNGC/C 345kV CB 7172","345kV GIS 보통점검","345kV GIS 보통점검","2020-10-28 09:00","2020-10-28 18:00","취소","취소","연속"]
[80,"경기북부","구리","포천LNGC/C 345kV CB 7172","345kV GIS 보통점검","345kV GIS 보통점검","2020-10-22 09:00","2020-10-22 18:00","2020-10-22 09:00","2020-10-22 18:00","연속"]
[81,"경기북부","직할","신의정부S/S 345kV #2 Sh.R","20~21년도 경기북부 직할 변전정비회사 총액공사","신의정부S/S #2 Sh.R 보호배전반 교체공사","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[82,"경기북부","직할","신의정부S/S #2 M.Tr","신의정부S/S 종합예방진단시스템 설치공사","주변압기 붓싱 누설전류, OLTC 부분방전 진단센서 설치","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[83,"경기북부","직할","신의정부S/S #3 M.Tr","신의정부S/S 종합예방진단시스템 설치공사","주변압기 붓싱 누설전류, OLTC 부분방전 진단센서 설치","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[84,"경기북부","직할","신가평신의정부#1 T/L","신의정부S/S 효성제 GIS 하자보수공사","신의정부S/S 345kV CB, 수동접지 측 제어케이블 경로변경","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[85,"경기북부","직할","신의정부S/S #4 M.Tr","신의정부S/S 종합예방진단시스템 설치공사","주변압기 붓싱 누설전류, OLTC 부분방전 진단센서 설치","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[86,"경기북부","직할","신의정부S/S #1 M.Tr","신의정부S/S 종합예방진단시스템 설치공사","주변압기 붓싱 누설전류, OLTC 부분방전 진단센서 설치","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[87,"경기북부","직할","양주S/S #3 M.Tr","양주S/S 154kV 옥외철구 변전설비 철거공사","○ #3M.Tr 휴전 후 STATCOM 부지설비 철거 - (구 옥외철구) 양주금촌 #1,2T/L, 양주고양 #2T/L CCT","2020-10-06 09:00","2020-10-07 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[88,"경기북부","직할","양주S/S #4 M.Tr","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-10-23 09:00","2020-10-24 18:00","2020-10-25 09:00","2020-10-26 18:00","연속"]
[89,"경기","군포","서서울#2신시흥#2 T/L","2020-2021년 송전정비회사 총액공사","- 스페이서간격조정:1335개","2020-10-13 08:00","2020-10-16 18:00","취소","취소","연속"]
[90,"경기","군포","신온양서서울#1 T/L","2020-2021년 군포전력 송전정비회사 총액공사","신온양서서울#1T/L 169~170호 항공장애표시구 설치 공사","2020-10-05 09:00","2020-10-05 18:00","2020-10-05 09:00","2020-10-05 18:00","연속"]
[91,"경기","군포","서서울S/S #3 M.Tr","서서울#1S/S 345kV #3M.Tr 대체공사","- #3M.Tr 철거 및 설치 / 케이블 포설 및 기타 부대공사 - 7600, 7672 GIS 조작, 6344 GIS 하자, 3499, 4379, 437-1,2 VCB 보통점검 - 3차측 절연보강","2020-10-27 09:00","2020-12-11 18:00","2020-10-27 09:00","2020-12-11 18:00","연속"]
[92,"경기","군포","서서울S/S #1 M.Tr","서서울S/S 73B/F PNL 대체 공사","서서울S/S 73B/F PNL 대체 공사","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[93,"경기","군포","신시흥신안산#2 T/L","2020-2021년 송전정비회사 총액공사","- 345kV 서서울2-신시흥#2T/L 스페이서간격조정 관련 안전이격거리확보","2020-10-13 08:00","2020-10-16 18:00","취소","취소","연속"]
[94,"경기","동부","곤지암동서울#1 T/L","20년 동부 변전정비회사 총액공사","곤지암:7371 GIS(보통),[곤지암-동서울#1T/L] 43L/R 회로보완 확인 및 Remote 회로분리 시행,LA(보통)7300(A,B,C)전자변교체,","2020-10-06 09:30","2020-10-06 18:00","2020-10-06 09:30","2020-10-06 18:00","연속"]
[95,"경기","성남","신성남#2S/S 345kV SEC CB 75760","20년 성남전력지사 변전정비회사 총액공사","조작시험, 전자변교체","2020-10-14 14:00","2020-10-14 18:00","2020-10-14 14:00","2020-10-14 18:00","연속"]
[96,"경기","성남","신성남#2S/S 345kV SEC CB 70710","20년 성남전력지사 변전정비회사 총액공사","조작시험, 전자변교체","2020-10-14 09:00","2020-10-14 14:00","2020-10-14 09:00","2020-10-14 14:00","연속"]
[97,"경기","성남","신수원S/S #1 M.Tr","20년 성남전력 변전정비회사 총액공사","#1S.Tr 대체","2020-10-27 09:00","2020-10-28 18:00","2020-10-27 09:00","2020-10-28 18:00","연속"]
[98,"경기","성남","신수원S/S #2 M.Tr","20년 성남전력 변전정비회사 총액공사","- 2차측 GIS(조작) 전자변교체 - 3차측 GIS(조작) - 2S.Tr(대체) - 1차 LA(대체) - 96P,D 커버 설치","2020-10-29 09:00","2020-10-30 18:00","2020-10-29 09:00","2020-10-30 18:00","연속"]
[99,"경기","성남","신수원S/S 345kV #2 BUS","신수원S/S 345kV 용량부족GIS 대체","- GIS 대체 * 3대","2020-10-12 09:00","2020-10-28 18:00","2020-10-12 09:00","2020-10-28 18:00","연속"]
[100,"경기","성남","신안성신성남#1 T/L","345kV 신용인-동서울T/L 지장철탑 이설공사(서울세종)","345kV 신용인-동서울T/L 7-1호 지장철탑 이설(요청자 시행 공사) - 교체구간 : 0.7km, 4회선 1기 본선로, 1기 임시선로 - 345kV 신안성-신성남T/L 64-1호 병가구간","2020-10-22 09:00","2020-11-04 18:00","취소","취소","연속"]
[101,"경기","성남","신안성신성남#2 T/L","345kV 신용인-동서울T/L 지장철탑 이설공사(서울세종)","345kV 신용인-동서울T/L 7-1호 지장철탑 이설(요청자 시행 공사) - 교체구간 : 0.7km, 4회선 1기 본선로, 1기 임시선로 - 345kV 신안성-신성남T/L 64-1호 병가구간","2020-10-06 09:00","2020-10-19 18:00","취소","취소","연속"]
[102,"경기","성남","신안성S/S 345kV #6 Sh.R","2020년 성남전력 변전정비 총액공사","보호반대체","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[103,"경기","성남","신용인S/S #4 M.Tr","CT단자함 제작사하자보수","CT단자함 제작사하자보수","2020-10-26 09:00","2020-10-26 18:00","취소","취소","연속"]
[104,"경기","성남","신용인동서울#1 T/L","345kV 신용인-동서울T/L 지장철탑 이설공사(서울세종)","345kV 신용인-동서울T/L 7-1호 지장철탑 이설(요청자 시행 공사) - 교체구간 : 0.7km, 4회선 1기 본선로, 1기 임시선로 - 345kV 신안성-신성남T/L 64-1호 병가구간","2020-10-22 09:00","2020-11-04 18:00","취소","취소","연속"]
[105,"경기","성남","신용인삼성 T/L","20년 성남전력 변전정비회사 총액공사","보호계전기 성능개선(유호)","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[106,"경기","성남","신용인동서울#2 T/L","345kV 신용인-동서울T/L 지장철탑 이설공사(서울세종)","345kV 신용인-동서울T/L 7-1호 지장철탑 이설(요청자 시행 공사) - 교체구간 : 0.7km, 4회선 1기 본선로, 1기 임시선로 - 345kV 신안성-신성남T/L 64-1호 병가구간","2020-10-06 09:00","2020-10-19 18:00","취소","취소","연속"]
[107,"경기","직할","화성S/S 345kV SEC CB 75760","20년 직할 변전정비회사 총액공사","화성S/S 75-76SEC GIS 하자 점검","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[108,"경기","직할","화성S/S 345kV SEC CB 70710","20년 직할 변전정비회사 총액공사","화성S/S 70-71SEC GIS 하자 점검","2020-10-05 09:00","2020-10-05 18:00","취소","취소","연속"]
[109,"경기","직할","화성신안산#1 T/L","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79Bay 환원작업","2020-10-05 08:00","2020-10-20 18:00","2020-10-05 08:00","2020-10-20 18:00","연속"]
[110,"경기","직할","화성S/S #2 M.Tr","20년 직할 변전정비회사 총액공사","화성 : #2M.Tr 1차 GIS 조작, 1차 LA, 3차 LA, PT 보통, 1차, 2차 부싱절연유 채유(A,B,C상)","2020-10-28 09:00","2020-10-28 18:00","2020-10-28 09:00","2020-10-28 18:00","연속"]
[111,"경기","직할","화성신안산#2 T/L","345kV 화성S/S GIS 용량대체공사","- 화성신안산#2T/L 7A -> 7B Bay 임시이설","2020-10-21 08:00","2020-11-07 18:00","2020-10-21 08:00","2020-11-07 18:00","연속"]
[112,"경기","직할","화성S/S 345kV CB 7671","20년 직할 변전정비회사 총액공사","화성S/S 화성-서서울 #1T/L, 화성-서서울#1T/L-TIE GIS 보통","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[113,"경기","직할","화성S/S 345kV #71 BUS","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79 Bay 선로환원 - #71BUS 무부하 가압 시행","2020-10-15 11:00","2020-10-16 11:00","2020-10-15 11:00","2020-10-16 11:00","연속"]
[114,"경기","직할","화성S/S 345kV #76 BUS","345kV 화성S/S GIS 용량대체공사","- 화성신안산#1T/L 7B -> 79 Bay 선로환원 - #76BUS 무부하 가압 시행","2020-10-16 11:00","2020-10-17 11:00","2020-10-16 11:00","2020-10-17 11:00","연속"]
[115,"경기","직할","화성S/S 345kV CB 7600","20년 직할 변전정비회사 총액공사","화성S/S 화성-서서울 #1T/L, 화성-서서울#1T/L-TIE GIS 보통","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[116,"경기","평택","고덕S/S #4 M.Tr","고덕S/S 345kV #4M.Tr 변압기 하자점검","고덕S/S 345kV #4M.Tr 변압기 하자점검 / #4M.Tr 2차 GIS 하자점검","2020-10-26 10:00","2020-10-28 18:00","2020-10-26 10:00","2020-10-28 18:00","연속"]
[117,"경기","평택","고덕S/S #3 M.Tr","고덕S/S 345kV #3M.Tr 변압기 하자점검","고덕S/S 345kV #3M.Tr 변압기 하자점검 / #3M.Tr 2차 GIS 하자점검","2020-10-19 10:00","2020-10-21 18:00","2020-10-19 10:00","2020-10-21 18:00","연속"]
[118,"경기","평택","고덕S/S #2 M.Tr","고덕S/S 345kV #2M.Tr 변압기 하자점검","고덕S/S 345kV #2M.Tr 변압기 하자점검 / #2M.Tr 2차 GIS 하자점검","2020-10-12 10:00","2020-10-14 18:00","2020-10-12 10:00","2020-10-14 18:00","연속"]
[119,"경기","평택","고덕S/S #1 M.Tr","고덕S/S 345kV #1M.Tr 변압기 하자점검","고덕S/S 345kV #1M.Tr 변압기 하자점검 / #1M.Tr 2차 GIS 하자점검","2020-10-05 10:00","2020-10-07 18:00","2020-10-05 10:00","2020-10-07 18:00","연속"]
[120,"강원","강릉","신양양S/S 345kV #2 BUS","신양양S/S 345kV BUS 계통전압 측정시험","- 모선 PT 변압비 측정","2020-10-19 13:00","2020-10-19 14:30","2020-10-19 13:00","2020-10-19 14:30","연속"]
[121,"강원","강릉","동해신양양 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 점퍼선 보수 : 345kV 양양양수T/L No. 19 등 18기 33개소, ○ 상간스페이서 설치 : 345kV 양양양수T/L No.162-163","2020-10-12 08:00","2020-10-16 18:00","2020-10-12 08:00","2020-10-16 18:00","매일"]
[122,"강원","강릉","신양양S/S #3 M.Tr","변압기 보통점검, 부싱 절연유 채유","변압기 보통점검, 부싱 절연유 채유","2020-10-26 10:00","2020-10-27 18:00","2020-10-26 10:00","2020-10-27 18:00","연속"]
[123,"강원","강릉","신양양S/S 345kV #1BUS","신양양S/S 345kV BUS 계통전압 측정시험","- 모선 PT 변압비 측정","2020-10-19 10:00","2020-10-19 12:00","2020-10-19 10:00","2020-10-19 12:00","연속"]
[124,"강원","강릉","동해양양PP T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 점퍼선 보수 : 345kV 양양양수T/L No.19 등 18기 33개소","2020-10-05 08:00","2020-10-08 18:00","2020-10-05 08:00","2020-10-08 18:00","매일"]
[125,"강원","강릉","양양P/P 345kV #1 BUS","양양P/P 345kV BUS 계통전압 측정시험","- 모선 PT 변압비 측정","2020-10-19 14:30","2020-10-19 16:00","2020-10-19 14:30","2020-10-19 16:00","연속"]
[126,"강원","강릉","양양P/P 345kV #2 BUS","양양P/P 345kV BUS 계통전압 측정시험","- 모선 PT 변압비 측정","2020-10-19 16:00","2020-10-19 17:30","2020-10-19 16:00","2020-10-19 17:30","연속"]
[127,"강원","동해","신제천동해#1 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","전선접속개소 해소 및 가공지선 불량개소 정비","2020-10-06 08:00","2020-10-18 18:00","2020-10-06 08:00","2020-10-18 18:00","연속"]
[128,"강원","동해","동해S/S 345kV CB 7672","2020년 동해변전소 362kV GIS 정밀점검공사","1. #3 M.TR 1차 GIS(7672) 정밀점검","2020-10-13 09:00","2020-10-16 18:00","2020-10-13 09:00","2020-10-16 18:00","연속"]
[129,"강원","동해","동해S/S 345kV CB 7671","2020년 동해변전소 362kV GIS 정밀점검공사","1. 동해-삼척GP#2 GIS(7671) 정밀점검","2020-10-19 09:00","2020-10-21 18:00","2020-10-19 09:00","2020-10-21 18:00","연속"]
[130,"강원","동해","동해S/S 345kV CB 7600","2020년 동해변전소 362kV GIS 정밀점검공사","1. 동해-삼척GP#2 T/L- #3M.TR 1차 TIE(7600) 정밀점검","2020-10-22 09:00","2020-10-24 18:00","2020-10-22 09:00","2020-10-24 18:00","연속"]
[131,"강원","동해","동해S/S 345kV CB 7571","2020년 동해변전소 362kV GIS 정밀점검공사","1. 동해-삼척GP#1 GIS (7571) 정밀점검","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[132,"강원","동해","동해S/S 345kV CB 7500","2020년 동해변전소 362kV GIS 정밀점검공사","1. 동해-삼척GP#1T/L- 동해-북평TP#3T/L TIE GIS (7500) 정밀점검","2020-10-29 09:00","2020-10-31 18:00","2020-10-29 09:00","2020-10-31 18:00","연속"]
[133,"강원","동해","신제천동해#2 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","전선접속개소 해소 및 불량애자 교체","2020-10-19 08:00","2020-10-31 18:00","2020-10-19 08:00","2020-10-31 18:00","연속"]
[134,"강원","동해","삼척T/P #3 Tie-Tr","2020년 동해전력 변전정비협력회사 총액공사","1. 3차 GIS 보통점검 2. 2,3차 LA 보통점검 3. 3차 PT 보통점검 4. M.Tr 보호반 보통점검 5. #2S.Tr 보통점검","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[135,"강원","동해","삼척T/P #2 Tie-Tr","2020년 동해전력 변전정비협력회사 총액공사","1. 3차 GIS 보통점검 2. 2,3차 LA 보통점검 3. 3차 PT 보통점검 4. M.Tr 보호반 보통점검 5. #1S.Tr 보통점검","2020-10-05 09:30","2020-10-06 18:00","2020-10-05 09:30","2020-10-06 18:00","연속"]
[136,"충북","직할","신진천S/S 345kV #2 BUS","345kV 신진천S/S 용량부족 GIS 대체공사 (#75BUS)","345kV GIS #75BUS 및 (#71~74BAY)52,02DS 대체(9차분)","2020-10-21 09:00","2020-11-15 18:00","취소","취소","연속"]
[137,"충북","청주","남청주S/S #3 M.Tr","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV 76BAY B/F PNL 교체 공사","2020-10-09 09:30","2020-10-11 18:00","2020-10-09 09:30","2020-10-11 18:00","연속"]
[138,"충북","청주","남청주S/S #1 M.Tr","2020년 하반기 345kV M.Tr 및 OLTC 정밀점검 공사","#1M.Tr 및 OLTC 정밀점검","2020-10-05 09:00","2020-10-18 18:00","2020-10-05 09:00","2020-10-18 18:00","연속"]
[139,"충북","청주","신중부남청주#1 T/L","20-21년 청주전력 변전정비 총액공사","6년 이상 장기사용 전자변 교체","2020-10-12 09:00","2020-10-13 18:00","취소","취소","매일"]
[140,"충북","청주","남청주S/S #3 M.Tr","2020년 하반기 345kV M.Tr 및 OLTC 정밀점검 공사","#3M.Tr 및 OLTC 정밀점검","2020-10-19 09:00","2020-11-01 18:00","2020-10-19 09:00","2020-11-01 18:00","연속"]
[141,"충북","청주","남청주S/S 345kV #1 BUS","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV CT 집합반 교체 공사","2020-10-24 09:00","2020-10-24 18:00","2020-10-24 09:00","2020-10-24 18:00","연속"]
[142,"충북","청주","남청주S/S 345kV #2 BUS","20-21년 청주전력 변전정비회사 총액공사","남청주S/S 345kV CT 집합반 교체 공사","2020-10-25 09:00","2020-10-25 18:00","2020-10-25 09:00","2020-10-25 18:00","연속"]
[143,"충북","청주","신옥천세종#2 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 72BAY B/F PNL 교체 공사","2020-10-05 09:30","2020-10-08 18:00","취소","취소","연속"]
[144,"충북","청주","신옥천북경남 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 72BAY B/F PNL 교체 공사","2020-10-05 09:30","2020-10-08 18:00","취소","취소","연속"]
[145,"충북","청주","신옥천S/S #1 M.Tr","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 71BAY B/F PNL 교체 공사","2020-10-12 09:30","2020-10-15 18:00","취소","취소","연속"]
[146,"충북","청주","신옥천세종#1 T/L","20-21년 청주전력 변전정비회사 총액공사","신옥천S/S 345kV 71BAY B/F PNL 교체 공사","2020-10-12 09:30","2020-10-15 18:00","취소","취소","연속"]
[147,"충북","충주","신제천S/S SVC CB (7271, 7200)","2020년 충주전력지사 소방시설 점검용역","신제천S/S SVC제어동 소방시설 작동기능점검","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[148,"충북","충주","신제천S/S SVC용 M.Tr 1차 GIS","2020년 충주전력지사 소방시설 점검용역","신제천S/S SVC제어동 소방시설 작동기능점검","2020-10-15 09:00","2020-10-15 18:00","취소","취소","연속"]
[149,"충북","충주","신충주S/S #4 M.Tr","신충주S/S 154kV GIS 설치공사(전문)","신충주S/S 154kV Sh.C용 GIS설치 × 2CCT","2020-10-13 09:00","2020-10-23 18:00","2020-10-13 09:00","2020-10-23 18:00","연속"]
[150,"대전충남","대전","신옥천신계룡 T/L","신계룡S/S 345kV 71B/F PNL 교체 및 병행작업","신계룡S/S 345kV 71B/F PNL 교체 및 병행작업","2020-10-05 09:00","2020-10-09 18:00","취소","취소","연속"]
[151,"대전충남","대전","신계룡청양 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-26 07:00","2020-10-30 18:00","취소","취소","연속"]
[152,"대전충남","대전","신계룡S/S #3 M.Tr","신계룡S/S 154kV Sh.C 조작용 GCB 설치공사 안전이격확보","신계룡S/S 154kV Sh.C 조작용 GCB 설치공사 안전이격확보","2020-10-13 09:00","2020-10-13 13:00","2020-10-13 09:00","2020-10-13 13:00","연속"]
[153,"대전충남","서산","북당진현대제철 T/L","345kV 신송산분기T/L 건설공사","345kV 현대제철T/L 임시선로 구성","2020-10-05 07:00","2020-10-08 19:00","2020-10-05 09:00","2020-10-23 15:00","연속"]
[154,"대전충남","서산","신당진개폐소현대제철 T/L","345kV 신송산분기T/L 건설공사","345kV 현대제철T/L 임시선로 구성","2020-10-09 07:00","2020-10-12 19:00","2020-10-26 09:00","2020-11-07 15:00","연속"]
[155,"대전충남","서산","신당진S/S #1 M.Tr","20년 서산P/O 변전정비 총액공사","신당진S/S 345kV #1M.Tr 보통점검 및 1,2,3차 LA 보통점검","2020-10-05 10:00","2020-10-08 18:00","2020-10-05 10:00","2020-10-08 18:00","연속"]
[156,"대전충남","서산","신당진S/S 345kV CB 7172","20년 장기 미동작 차단기 조작시험","신당진S/S 345kV 신서산신당진#1T/L 7172 CB 조작시험","2020-10-12 10:00","2020-10-12 14:00","2020-10-12 10:00","2020-10-12 14:00","연속"]
[157,"대전충남","서산","신당진S/S 345kV CB 7400","20년 장기 미동작 차단기 조작시험","신당진S/S 345kV 신당진연락#1T/L-#1 M.Tr 1차 TIE 7400 CB 조작시험","2020-10-12 14:00","2020-10-12 18:00","2020-10-12 14:00","2020-10-12 18:00","연속"]
[158,"대전충남","서산","신당진S/S #2 M.Tr","20년 서산P/O 변전정비 총액공사","신당진S/S 345kV #2M.Tr 보통점검 및 1,2,3차 LA 보통점검, B상 누유보수","2020-10-26 10:00","2020-10-30 18:00","2020-10-26 10:00","2020-10-30 18:00","연속"]
[159,"대전충남","서산","신서산S/S 345kV #5 Sh.R","20년 서산P/O 변전정비 총액공사","신서산S/S 345kV #5Sh.R 오일펌프교체","2020-10-05 10:00","2020-10-07 18:00","2020-10-05 10:00","2020-10-07 18:00","연속"]
[160,"대전충남","서산","신서산신당진#1 T/L","345신서산-신당진#1T/L 점검 및 정비","- No.29~30 : 스페이서댐퍼 키퍼 풀림개소 점검 및 정비 - No.11,28 : 기타 불량개소 정비","2020-10-12 08:00","2020-10-12 18:00","취소","취소","연속"]
[161,"대전충남","서산","신서산아산#2 T/L","345신서산-신당진#1T/L 점검 및 정비 (4회선 병가구간)","- No.29~30 : 스페이서댐퍼 키퍼 풀림개소 점검 및 정비 - No.11,28 : 기타 불량개소 정비","2020-10-12 08:00","2020-10-12 18:00","취소","취소","연속"]
[162,"대전충남","서산","신서산S/S 345kV CB 7572","20년 서산P/O 345kV GIS정밀점검공사","신서산S/S 345kV 신서산-태안화력#2T/L 7572 GIS 정밀점검","2020-10-12 10:00","2020-10-16 18:00","2020-10-12 10:00","2020-10-16 18:00","연속"]
[163,"대전충남","서산","신서산신당진#2 T/L","345신서산-신당진#2T/L 점검 및 정비","- No.42 : 아크발생 관련 설비점검","2020-10-13 08:00","2020-10-13 18:00","취소","취소","연속"]
[164,"대전충남","서산","신서산아산#1 T/L","345kV 신서산-아산#1T/L 소도체 이도조정 공사","이도조정 공사 : No.48-50,69-70(2개소)","2020-10-14 08:00","2020-10-14 18:00","취소","취소","연속"]
[165,"대전충남","서산","신서산S/S 345kV CB 7672","20년 서산P/O 345kV GIS정밀점검공사","신서산S/S 345kV 신서산-태안화력#1T/L 7672 GIS 정밀점검","2020-10-19 10:00","2020-10-23 18:00","2020-10-19 10:00","2020-10-23 18:00","연속"]
[166,"대전충남","서산","신서산S/S 345kV CB 7600","20년 서산P/O 345kV GIS정밀점검공사","신서산S/S 345kV 신서산-태안화력#1T/L - #3M.Tr TIE 7600 GIS 정밀점검","2020-10-26 10:00","2020-10-30 18:00","2020-10-26 10:00","2020-10-30 18:00","연속"]
[167,"대전충남","서산","신서산S/S 345KV #4 Sh.R","신서산S/S 345kV #4Sh.R 교체공사","신서산S/S 345kV #4Sh.R 교체공사","2020-10-22 09:00","2020-12-07 18:00","2020-10-22 09:00","2020-12-07 18:00","연속"]
[168,"대전충남","아산","청양신온양#2 T/L","345kV 북당진-신탕정T/L OPGW 시설공사(2구간)","345kV 청양-신탕정T/L No.146~147 항공구 5식 교체","2020-10-18 07:00","2020-10-18 18:00","취소","취소","연속"]
[169,"대전충남","아산","신온양신탕정#2 T/L","신탕정S/S 345kV #4M.Tr 증설공사","신탕정S/S 345kV #4M.Tr 증설공사","2020-10-13 11:00","2020-10-15 16:00","2020-10-13 11:00","2020-10-15 16:00","연속"]
[170,"대전충남","아산","청양신탕정 T/L","345kV 북당진-신탕정T/L OPGW 시설공사(2구간)","345kV 청양-신탕정T/L No.146~147 항공구 6식 교체","2020-10-17 07:00","2020-10-17 18:00","취소","취소","연속"]
[171,"대전충남","아산","아산S/S 345kV CB 7171","아산S/S 345KV 현대제 GIS 공기조작부 성능개선공사","- 공기조작부 컨트롤블럭 철거 공장점검입고 - 점검완료분 설치 - 차단기 개폐타임","2020-10-06 09:00","2020-10-08 18:00","2020-10-06 09:00","2020-10-08 18:00","연속"]
[172,"대전충남","아산","아산S/S 345kV CB 7200","아산S/S 345KV 현대제 GIS 공기조작부 성능개선공사","- 공기조작부 컨트롤블럭 철거 공장점검입고 - 점검완료분 설치 - 차단기 개폐타임","2020-10-29 09:00","2020-10-31 18:00","2020-10-29 09:00","2020-10-31 18:00","연속"]
[173,"대전충남","아산","아산S/S 345kV CB 7271","아산S/S 345KV 현대제 GIS 공기조작부 성능개선공사","- 공기조작부 Controcl Block 철거 공장점검입고 - 점검완료분 설치 - 차단기 개폐타임","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[174,"대전충남","아산","아산S/S #2 M.Tr","아산S/S 345kV #2M.Tr B상 보통점검 및 누유보수","아산S/S 345kV #2M.Tr B상 보통점검 및 누유보수, 1,2차 GIS 보통점검, 부싱절연유 채유, 3차PT 점검","2020-10-19 09:00","2020-10-21 18:00","2020-10-19 09:00","2020-10-21 18:00","연속"]
[175,"대전충남","아산","아산S/S 345kV CB 7272","아산S/S 345KV 현대제 GIS 공기조작부 성능개선공사","- 공기조작부 컨트롤블럭 철거 공장점검입고 - 점검완료분 설치 - 차단기 개폐타임","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","연속"]
[176,"대전충남","청양","아산보령TP#2 T/L","[송전]345kV 청양-보령 등 9개TL 항공장애표시구 정비공사","345kV 아산-보령화력#2T/L 항공장애표시구 설치 - No.4~5, 27~28, 28~29, 31~32, 55~56, 58~59, 64~65, 76~77,86~87 (9경간)","2020-10-15 07:00","2020-10-19 18:00","취소","취소","매일"]
[177,"대전충남","청양","청양군산#1 T/L","[송전]345kV 청양-보령 등 9개TL 항공장애표시구 정비공사","345kV 청양-군산#1T/L 항공장애표시구 설치 - No.72~73, 73~74, 105~106, 113~114, 118~119, 126~127, 128~129, 131~132, 143~144, 144~145, 157~158, 158~159, 159~160, 165`166(14경간)","2020-10-19 07:00","2020-10-23 18:00","취소","취소","매일"]
[178,"대전충남","청양","청양S/S 345kV CB 7571","345,154kV 효성제 공압식 차단기 전자변 교체공사","345,154kV 효성제 공압식 차단기 전자변 교체공사","2020-10-08 09:00","2020-10-08 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[179,"대전충남","청양","신옥천청양 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-12 07:00","2020-10-16 18:00","취소","취소","연속"]
[180,"대전충남","청양","청양보령TP#1 T/L","청양S/S 345kV #71BAY B/F 보호반 대체","청양S/S 345kV #71BAY B/F 보호반 대체","2020-10-26 09:00","2020-10-30 18:00","취소","취소","연속"]
[181,"대전충남","청양","청양S/S 345kV CB 7672","345,154kV 효성제 공압식 차단기 전자변 교체공사","345,154kV 효성제 공압식 차단기 전자변 교체공사","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[182,"대전충남","청양","청양S/S 345kV CB 7600","345,154kV 효성제 공압식 차단기 전자변 교체공사","345,154kV 효성제 공압식 차단기 전자변 교체공사","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[183,"대전충남","청양","청양S/S 345kV CB 7500","345,154kV 효성제 공압식 차단기 전자변 교체공사","345,154kV 효성제 공압식 차단기 전자변 교체공사","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[184,"전북","군산","군산S/S 345kV #2 BUS","345kV 군산S/S Sh.R 설치공사","345kV 군산S/S Sh.R 설치공사 [휴전개소 : #75BUS] [작업개소 : 76BAY]","2020-10-07 09:00","2020-10-16 18:00","2020-10-07 09:00","2020-10-16 18:00","연속"]
[185,"전북","군산","군산새만금#2 T/L","345kV 군산S/S Sh.R 설치공사 (시험가압)","***무부하가압 선로(#70BUS) 345kV 군산S/S Sh.R 설치공사","2020-10-27 09:00","2020-10-28 18:00","2020-10-27 09:00","2020-10-28 18:00","연속"]
[186,"전북","군산","군산S/S 345kV #1 BUS","345kV 군산S/S Sh.R 설치공사","345kV 군산S/S Sh.R 설치공사 [휴전개소 : #70BUS] [작업개소 : 76BAY]","2020-10-19 09:00","2020-10-28 18:00","2020-10-19 09:00","2020-10-28 18:00","연속"]
[187,"전북","군산","군산새만금#2 T/L","345kV 군산S/S Sh.R 설치공사 (시험가압)","***무부하가압 선로(#75BUS) 345kV 군산S/S Sh.R 설치공사","2020-10-15 09:00","2020-10-16 18:00","2020-10-15 09:00","2020-10-16 18:00","연속"]
[188,"전북","군산","새만금S/S #3 M.Tr","새만금S/S 종합예방진단시스템 구축공사","새만금S/S #3M.Tr 종합예방진단시스템 구축공사","2020-10-29 09:00","2020-10-30 18:00","취소","취소","연속"]
[189,"전북","군산","새만금S/S #2 M.Tr","새만금S/S 종합예방진단시스템 구축공사","새만금S/S #2M.Tr 종합예방진단시스템 구축공사","2020-10-27 09:00","2020-10-28 18:00","취소","취소","연속"]
[190,"전북","군산","새만금S/S #2 M.Tr","'20년 군산P/O 170kV GIS 정밀점검공사","새만금S/S 345kV #2M.Tr 2차 GIS 정밀점검공사","2020-10-05 09:00","2020-10-06 18:00","취소","취소","연속"]
[191,"전북","김제","신김제S/S #3 M.Tr","154kV #1,2,3Sh.C 차단부 제작사 정밀점검 (안전이격)","- 차단부 철거 후 제작사 입고 - 제작사 정밀점검 후 설치","2020-10-27 09:00","2020-10-30 18:00","취소","취소","연속"]
[192,"전북","김제","신김제S/S #1 M.Tr","신김제S/S 노후 170GIS 교체 및 인출송전 재배열 공사(안전이격)","- 장기사용 노후 170GIS 교체공사 - 송전선로 인출 BAY 조정 - 기타 부대공사 1식","2020-10-05 09:00","2020-10-26 18:00","2020-10-05 09:00","2020-10-29 18:00","연속"]
[193,"전북","직할","신옥천신남원#2 T/L","345kV 신옥천-신남원#2T/L 정밀점검 공사","□ 345kV 신옥천-신남원T/L No.1~178(187기) ○ 정밀점검 : 기초, 지지물, 애자, 금구류 및 기타 부대설비 점검 ○ 기초점검 : 부재변형, 석축, 옹벽, 매설지선 노출 여부 등 ○ 지장수목 여부 확인 및 애자련 금구류 체결상태 등","2020-10-15 08:00","2020-10-30 18:00","2020-10-12 08:00","2020-10-27 18:00","매일"]
[194,"전북","직할","신남원S/S #1 M.Tr","신남원S/S #1M.Tr 23kV PT 교체 공사","송운(변전)-51 관련, 유사고장 삼능제 PT 교체 공사","2020-10-30 09:00","2020-10-30 18:00","취소","취소","연속"]
[195,"전북","직할","신남원의령#2 T/L","신남원S/S GAS 누기보수공사(7452/7471)","신남원S/S GAS 누기보수공사 [휴전개소 : 신남원-의령#2T/L, #70BUS)] [작업개소 : 7452DS(A/B/C), 7471(B)]","2020-10-21 09:00","2020-10-24 18:00","2020-10-21 09:00","2020-10-24 18:00","연속"]
[196,"전북","직할","신남원S/S 345kV #2 BUS","신남원S/S GAS 누기보수공사(#75BUS)","신남원S/S GAS 누기보수공사 [휴전개소 : #75BUS] [작업개소] - 7600(04/28~05/21) - 7272(05/02~05/13) - 7352/7452(05/14~05/25) - 7500(06/03~06/14)","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[197,"전북","직할","신남원의령#1 T/L","신남원S/S GAS 누기보수공사(7371)","신남원S/S GAS 누기보수공사 [휴전개소 : 신남원-의령#1T/L, #70BUS] [작업개소 : 7371(A)]","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[198,"광주전남","강진","신화순신강진#1 T/L","2020년 가공송전 순시점검 위탁공사(강진전력지사)","345kV 신화순-신강진#1T/L 송전선로 정밀점검","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","매일"]
[199,"광주전남","강진","신화순신강진#2 T/L","2020년 가공송전 순시점검 위탁공사(강진전력지사)","345kV 신화순-신강진#2T/L 송전선로 정밀점검","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","매일"]
[200,"광주전남","강진","신강진S/S #4 M.Tr","'20-21년 강진전력지사 변전정비회사 총액공사","신강진S/S #4M.Tr 1차 부싱 절연열화 측정","2020-10-29 10:00","2020-10-29 17:00","2020-11-03 10:00","2020-11-04 17:00","연속"]
[201,"광주전남","광주","신광주S/S 345kV CB 7100","2020년 신광주S/S 345kV GIS 정밀점검","신광주S/S 345kV 7100CB 정밀점검","2020-10-06 09:00","2020-10-09 18:00","취소","취소","연속"]
[202,"광주전남","광주","신광주S/S 345kV CB 7172","2020년 신광주S/S 345kV GIS 정밀점검","신광주S/S 345kV 7172CB 정밀점검","2020-10-12 09:00","2020-10-15 18:00","취소","취소","연속"]
[203,"광주전남","광주","신광주S/S #1 M.Tr","신광주S/S #1M.Tr 보호반 교체 및 345kV GIS 정밀점검","신광주S/S #1M.Tr 보호반 교체, 7100 및 7172 CB 정밀점검","2020-10-05 10:00","2020-10-16 18:00","2020-10-05 10:00","2020-10-16 18:00","연속"]
[204,"광주전남","순천","광양하동TP#1 T/L","20~21년 순천전력 송전정비회사 총액공사","○ 345kV 신강진-광양#2T/L 전력선교체 관련 - 4회선 병가구간 안전거리 확보 휴전","2020-10-21 07:00","2020-10-22 18:00","2020-10-21 07:00","2020-10-22 18:00","연속"]
[205,"광주전남","순천","광양S/S #3 M.Tr","20-21년 변전정비회사 총액공사","광양SS #3M.Tr 1차 7772 GIS 초기점검","2020-10-28 09:00","2020-10-28 18:00","2020-10-28 09:00","2020-10-28 18:00","연속"]
[206,"광주전남","순천","신강진광양#2 T/L","20~21년 순천전력 송전정비회사 총액공사","○ 345kV 신강진-광양#2T/L 전선접속개소해소 - 283~286호간 전력선 교체","2020-10-21 07:00","2020-10-25 18:00","2020-10-21 07:00","2020-10-25 18:00","연속"]
[207,"광주전남","순천","광양S/S #1 M.Tr","20년(하) 순천전력지사 170kV GIS 정밀점검공사","광양S/S #1M.Tr 2차 GIS 정밀점검(CB,상부모선)","2020-10-18 09:00","2020-10-19 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[208,"광주전남","순천","광양S/S #2 M.Tr","20년(하) 순천전력지사 170kV GIS 정밀점검공사","광양S/S #2M.Tr 2차 GIS 정밀점검(CB,상부모선)","2020-10-20 09:00","2020-10-21 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[209,"광주전남","순천","신강진광양#1 T/L","20~21년 순천전력 송전정비회사 총액공사","○ 345kV 신강진-광양#1T/L 전선접속개소해소 - 283~286호간 전력선 교체","2020-10-17 07:00","2020-10-20 18:00","2020-10-17 07:00","2020-10-20 18:00","연속"]
[210,"광주전남","순천","광양하동TP#2 T/L","20~21년 순천전력 송전정비회사 총액공사","○ 345kV 신강진-광양#1T/L 전력선교체 관련 - 4회선 병가구간 안전거리 확보 휴전","2020-10-19 07:00","2020-10-20 18:00","취소","취소","연속"]
[211,"광주전남","순천","광양S/S 345kV #75 BUS","광양S/S 362kV GIS 용량대체공사(#75BUS측)","○ 광양S/S 362kV GIS 용량대체공사 - #75 BUS 및 DS(71~73BAY) 대체(50kA → 63kA)","2020-11-02 09:00","2020-12-04 18:00","취소","취소","연속"]
[212,"광주전남","순천","율촌CC여수TP T/L","여수화력S/Y #4M.Tr 및 SW증설공사","ㅇ345kV #4M.Tr 증설 ㅇ광양CC-여수TP #1,2T/L SW증설 ㅇ기타부대공사 1식","2020-10-26 10:00","2020-10-30 18:00","2020-10-26 10:00","2020-10-30 18:00","연속"]
[213,"광주전남","순천","광양여수TP T/L","여수화력S/Y #4M.Tr 및 SW증설공사","ㅇ345kV #4M.Tr 증설 ㅇ광양CC-여수TP #1,2T/L SW증설 ㅇ기타부대공사 1식","2020-10-19 10:00","2020-10-23 18:00","2020-10-12 10:00","2020-10-16 18:00","연속"]
[214,"광주전남","순천","여수T/P #3 Tie-Tr","20-21년 변전정비회사 총액공사","여수화력S/Y #3M.Tr 96D 기계적 보호장치 배선 루트변경","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[215,"광주전남","순천","광양S/S 345kV #70 BUS","광양S/S 362kV GIS 용량대체공사","○ 광양S/S 362kV GIS 용량대체공사 - #70 BUS 및 DS(71~73BAY) 대체(50kA → 63kA)","2020-09-03 09:00","2020-10-16 18:00","취소","취소","연속"]
[216,"대구","경산","신경산대구#1 T/L","20-21년도 경산전력지사 가공송전정비회사 총액공사","애자교체 : No.99","2020-10-19 13:00","2020-10-20 12:00","2020-10-19 13:00","2020-10-20 12:00","연속"]
[217,"대구","경산","신경산대구#2 T/L","20-21년도 경산전력지사 가공송전정비회사 총액공사","애자교체 : No.99","2020-10-19 07:30","2020-10-19 12:00","2020-10-19 07:30","2020-10-19 12:00","연속"]
[218,"대구","경산","신경산S/S #4 M.Tr","2020년 345 신경산 주변압기 정밀","-주변압기정밀","2020-10-12 09:00","2020-10-20 18:00","2020-10-12 09:00","2020-10-20 18:00","연속"]
[219,"대구","달성","북경남고령#2 T/L","20-21년 가공송전정비회사 총액공사","애자련 교체(No.68,71,74)","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[220,"대구","달성","서대구고령#1 T/L","고령S/S 345kV 7671, 7600 차단기 동작시험 및 LA 점검","고령S/S 345kV 7671, 7600 차단기 동작시험 및 LA 점검","2020-10-12 09:00","2020-10-12 18:00","2020-10-12 09:00","2020-10-12 18:00","연속"]
[221,"대구","달성","고령의령#1 T/L","고령S/S 345kV 7372 CB 정밀점검[Test 선로]","고령S/S 345kV 7372 CB 정밀점검[Test 선로]","2020-10-08 13:00","2020-10-08 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[222,"대구","달성","북경남고령#1 T/L","고령S/S 345kV 7871, 7800 차단기 동작시험 및 LA 점검","고령S/S 345kV 7871, 7800 차단기 동작시험 및 LA 점검","2020-10-19 09:00","2020-10-19 18:00","2020-10-19 09:00","2020-10-19 18:00","연속"]
[223,"대구","칠곡","북대구S/S 345kV CB 7400","북대구S/S 345kV GIS 보통점검","북대구S/S 345kV GIS 보통점검","2020-10-08 09:30","2020-10-08 18:00","2020-10-08 09:30","2020-10-08 18:00","연속"]
[224,"대구","칠곡","북대구S/S #1 M.Tr","북대구S/S 154kV #1 BUS-PRO PNL 대체공사","북대구S/S 154kV #1 BUS-PRO PNL 대체공사","2020-10-15 10:30","2020-10-15 11:00","2020-10-15 10:30","2020-10-15 11:00","연속"]
[225,"대구","칠곡","북대구S/S #2 M.Tr","북대구S/S 154kV #2 BUS-PRO PNL 대체공사","북대구S/S 154kV #2 BUS-PRO PNL 대체공사","2020-10-22 10:00","2020-10-22 10:30","2020-10-22 10:00","2020-10-22 10:30","연속"]
[226,"대구","칠곡","북대구S/S 345kV #2 BUS","북대구S/S #75BUS 모선보호반 교체작업","북대구S/S #75BUS 모선보호반 교체작업","2020-10-26 09:30","2020-10-30 18:00","2020-10-26 09:30","2020-10-30 18:00","연속"]
[227,"대구","칠곡","북대구S/S #3 M.Tr","북대구S/S 154kV #2 BUS-PRO PNL 대체공사","북대구S/S 154kV #2 BUS-PRO PNL 대체공사","2020-10-22 15:00","2020-10-22 15:30","2020-10-22 15:00","2020-10-22 15:30","연속"]
[228,"대구","포항","신포항신영일 T/L","신영일S/S 77B/F PNL 대체 작업","신영일S/S 77B/F PNL 대체 작업","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[229,"대구","포항","신영일S/S #4 M.Tr","신영일S/S 77B/F PNL 대체작업","신영일S/S 77B/F PNL 대체작업","2020-10-26 09:00","2020-10-26 18:00","2020-10-26 09:00","2020-10-26 18:00","연속"]
[230,"대구","포항","신포항S/S #4 M.Tr","신포항S/S 154kV 옥외철구 설비 GIS화 공사","- 인출 2단 POST측 상부계탑 대체 및 상부 BEAM 1기 철거 - 변압기 보호반 회로보완, 철구보강, 제어케이블 포결선 - 변압기 2차측 옥외철구에서 GIS로 부하이양 - CB,DS,가대,모선,금구류,케이블 철거 - 변압기 2차측 모선배선, 가공지선 대체 및 수직분기선 GIS부싱 연결 - 1호철탑에서 ST철구간 인출변경(송전)","2020-10-19 08:00","2020-10-23 18:00","2020-10-19 08:00","2020-10-23 18:00","연속"]
[231,"대구","포항","신포항S/S #2 M.Tr","신포항S/S 154kV 옥외철구 설비 GIS화 공사","- 인출 2단 POST측 상부계탑 대체 및 상부 BEAM 1기 철거 - 변압기 보호반 회로보완, 철구보강, 제어케이블 포결선 - 변압기 2차측 옥외철구에서 GIS로 부하이양 (GIS로 가압) - 변압기 2차측 상부모선 및 금구류 철거 - 변압기 2차측 모선배선, 가공지선 대체 및 수직분기선 GIS부싱 연결 - CB, DS, 기기가대, ILC PNL","2020-10-12 08:00","2020-10-16 18:00","2020-10-12 08:00","2020-10-16 18:00","연속"]
[232,"대구","포항","신울산월성NP#1 T/L","월성S/Y 7771 CB 보통점검 및 신울상-월성T/L 보호반 성능개선","월성S/Y 7771 CB 보통점검 및 신울상-월성T/L 보호반 성능개선","2020-10-07 09:30","2020-10-07 18:00","2020-10-07 09:30","2020-10-07 18:00","연속"]
[233,"대구","포항","월성1N/P 345kV #70 BUS","월성S/Y 70BUS 모선보호반 PNL 대체","월성S/Y 70BUS 모선보호반 PNL 대체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[234,"대구","포항","월성1N/P 345kV SEC CB 70710","월성S/Y 70BUS 모선보호반 PNL 대체","월성S/Y 70BUS 모선보호반 PNL 대체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[235,"대구","포항","월성1N/P 345kV CB 7371","월성S/Y 70BUS 모선보호반 PNL 대체","월성S/Y 70BUS 모선보호반 PNL 대체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[236,"대구","포항","월성1N/P 345kV CB 7271","월성S/Y 70BUS 모선보호반 PNL 대체","월성S/Y 70BUS 모선보호반 PNL 대체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[237,"대구","포항","월성1N/P 345kV CB 7471","월성S/Y 70BUS 모선보호반 PNL 대체","월성S/Y 70BUS 모선보호반 PNL 대체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[238,"대구","포항","월성1N/P 345kV CB 7400","월성S/Y 7400,7472 차단기 보통점검","월성S/Y 7400,7472 차단기 보통점검","2020-10-20 09:30","2020-10-20 18:00","2020-10-21 09:30","2020-10-21 18:00","연속"]
[239,"대구","포항","월성1N/P 345kV CB 7300","월성S/Y 7300,7372 보통점검","월성S/Y 7300,7372 보통점검","2020-10-06 09:30","2020-10-06 18:00","2020-10-06 09:30","2020-10-06 18:00","연속"]
[240,"대구","포항","월성1N/P 345kV CB 7372","월성S/Y 7300,7372 보통점검","월성S/Y 7300,7372 보통점검","2020-10-06 09:30","2020-10-06 18:00","2020-10-06 09:30","2020-10-06 18:00","연속"]
[241,"대구","포항","월성1N/P 345kV CB 7472","월성S/Y 7400,7472 차단기 보통점검","월성S/Y 7400,7472 차단기 보통점검","2020-10-20 09:30","2020-10-20 18:00","2020-10-21 09:30","2020-10-21 18:00","연속"]
[242,"경북","직할","안동C/C #1 Tie-Tr","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S 345kV M.Tr YPP제 보호반 성능개선 작업","2020-10-29 09:00","2020-10-29 18:00","2020-10-29 09:00","2020-10-29 18:00","연속"]
[243,"경북","직할","안동C/C 345kV CB 7372","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S UNIT #1 M.Tr 2차 GIS(7372) 조작시험","2020-10-20 12:00","2020-10-20 15:00","2020-10-20 12:00","2020-10-20 15:00","연속"]
[244,"경북","직할","안동C/C 345kV CB 7300","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S 신영일-안동CC T/L - UNIT #1 M.Tr 1차 TIE GIS(7300) 조작시험","2020-10-20 09:00","2020-10-20 12:00","2020-10-20 09:00","2020-10-20 12:00","연속"]
[245,"경북","직할","안동C/C 345kV CB 7371","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S 안동CC-신영일 T/L GIS(7371) 조작시험","2020-10-19 14:00","2020-10-19 18:00","2020-10-19 14:00","2020-10-19 18:00","연속"]
[246,"경북","직할","안동C/C 345kV CB 7271","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S 안동CC-신영주 T/L GIS(7271) 조작시험","2020-10-19 09:00","2020-10-19 14:00","2020-10-19 09:00","2020-10-19 14:00","연속"]
[247,"경북","직할","청송P/P #1 M.Tr","20~21년 경북본부 직할 변전정비회사 총액공사","청송양수S/Y 71 BAY B/F PNL 교체","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[248,"경북","직할","신영주청송PP T/L","20~21년 경북본부 직할 변전정비회사 총액공사","청송양수S/Y 71 BAY B/F PNL 교체","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[249,"경북","직할","청송P/P 345kV CB 7272","20~21년 경북본부 직할 변전정비회사 총액공사","청송양수S/Y 7272 GIS 조작시험","2020-10-28 15:00","2020-10-28 18:00","2020-10-28 15:00","2020-10-28 18:00","연속"]
[250,"경북","직할","청송P/P 345kV CB 7271","20~21년 경북본부 직할 변전정비회사 총액공사","청송양수S/Y 7271 GIS 조작시험","2020-10-28 09:00","2020-10-28 12:00","2020-10-28 09:00","2020-10-28 12:00","연속"]
[251,"경북","직할","청송P/P 345kV CB 7200","20~21년 경북본부 직할 변전정비회사 총액공사","청송양수S/Y 7200 GIS 조작시험","2020-10-28 12:00","2020-10-28 15:00","2020-10-28 12:00","2020-10-28 15:00","연속"]
[252,"부산울산","동부산","고리N/P 345kV CB 7872","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7872)","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[253,"부산울산","동부산","고리N/P 345kV CB 7A71","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7A71)","2020-10-05 09:00","2020-10-09 18:00","2020-10-05 09:00","2020-10-09 18:00","연속"]
[254,"부산울산","동부산","고리N/P 345kV CB 7800","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7800)","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[255,"부산울산","동부산","고리2N/P 345kV #71 BUS","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7177 - 2시간)","2020-10-16 16:00","2020-10-16 18:00","2020-10-16 16:00","2020-10-16 18:00","연속"]
[256,"부산울산","동부산","고리2N/P 345kV #71 BUS","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7A71 - 2시간)","2020-10-09 16:00","2020-10-09 18:00","2020-10-09 16:00","2020-10-09 18:00","연속"]
[257,"부산울산","동부산","고리NP#1고리NP#2 #1 T/L","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7177) - #1CLR","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[258,"부산울산","동부산","고리2N/P 345kV #70 BUS","345kV 고리N/P S/W 증설공사","1. 765kV 신고리S/S #4M.Tr 증설관련 345kV 2차측 GIS 증설 : #70BUS 2. 시험가압 : #71BUS→#70BUS→7451DS(#71BUS측 기기조작 없음)","2020-10-19 09:00","2020-11-02 18:00","2020-10-19 09:00","2020-11-02 18:00","연속"]
[259,"부산울산","동부산","신고리고리NP#2 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 항공구 설치 : 5~7호 백색구 9개","2020-10-27 14:00","2020-10-27 18:00","2020-10-27 14:00","2020-10-27 18:00","연속"]
[260,"부산울산","동부산","신고리고리NP#1 T/L","동부산전력지사 관내 OPGW 항공장애표시구 설치공사","345kV 신고리-고리NP#1T/L No.2호∼No.4호 구간 항공장애표시구(백색) 10개 설치","2020-10-28 08:00","2020-10-28 18:00","2020-10-28 08:00","2020-10-28 18:00","연속"]
[261,"부산울산","동부산","신고리고리NP#3 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 항공구 설치 : 5~7호 적색구 11개","2020-10-27 08:00","2020-10-27 14:00","2020-10-27 08:00","2020-10-27 14:00","연속"]
[262,"부산울산","동부산","신양산신대연#2 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 피뢰기 설치 : 1~26호 78SET","2020-10-29 08:00","2020-11-04 18:00","취소","취소","연속"]
[263,"부산울산","동부산","신양산북부산#2 T/L","345㎸ 신양산-북부산T/L OPGW 증설공사","345㎸ 신양산-북부산#2T/L OPGW 21.950㎞(120SQ/48C) 시설, S/T↔ICT실간 비금속광케이블 0.83㎞ 등 부대설비 1식","2020-10-12 07:00","2020-10-27 18:00","2020-10-12 07:00","2020-10-27 18:00","연속"]
[264,"부산울산","동부산","신양산S/S #3 M.Tr","[철거3차] 345kV 신양산S/S 현대화 일반공사","#3M.Tr 2차측 옥외철구 설비 철거","2020-10-12 08:00","2020-10-16 18:00","2020-10-26 08:00","2020-10-30 18:00","연속"]
[265,"부산울산","동부산","신양산S/S #2 M.Tr","[철거2차] 345kV 신양산S/S 현대화 일반공사","#2M.Tr 2차측 옥외철구 설비 철거","2020-10-05 08:00","2020-10-09 18:00","2020-10-19 08:00","2020-10-23 18:00","연속"]
[266,"부산울산","동부산","신양산S/S #4 M.Tr","[철거4차] 345kV 신양산S/S 현대화 일반공사","#4M.Tr 2차측 옥외철구 설비 철거","2020-10-19 08:00","2020-10-23 18:00","취소","취소","연속"]
[267,"부산울산","북부산","북부산S/S 345kV CB 7971","20-21 북부산전력지사 변전총액공사","북부산S/S 345kV 서부산-북부산#2T/L 7971 GIS 하자점검(단독차단기)","2020-10-05 10:00","2020-10-05 18:00","2020-10-05 10:00","2020-10-05 18:00","연속"]
[268,"부산울산","북부산","북부산S/S #2 M.Tr","20-21 북부산전력지사 변전총액공사","북부산S/S 345kV #2M.Tr 하자점검","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[269,"부산울산","북부산","북부산S/S #1 M.Tr","20-21 북부산전력지사 변전총액공사","북부산S/S 345kV #1M.Tr 2차 GIS(6144) 하자점검","2020-10-21 09:00","2020-10-22 18:00","2020-10-21 09:00","2020-10-22 18:00","연속"]
[270,"부산울산","북부산","북부산신울산#1 T/L","345kV 북부산-신울산#1T/L 노후 금구류 및 전선교체공사","345kV 북부산-신울산#1T/L 노후 금구류 및 전선교체공사(1~89호, 25경간 9.188C-km)","2020-10-28 07:30","2020-11-17 18:00","2020-10-28 07:30","2020-11-17 18:00","연속"]
[271,"부산울산","서부산","서부산S/S 345kV #1 Sh.R","서부산S/S 345kV #7177 GIS 차단기동작시험","서부산S/S 345kV #7177 GIS 차단기동작시험","2020-10-16 10:00","2020-10-16 18:00","2020-10-16 10:00","2020-10-16 18:00","연속"]
[272,"부산울산","서부산","서부산S/S 345kV CB 7171","서부산S/S 345kV #7171 GIS 차단기동작시험","서부산S/S 345kV #7171 GIS 차단기동작시험","2020-10-14 10:00","2020-10-14 18:00","2020-10-14 10:00","2020-10-14 18:00","연속"]
[273,"부산울산","서부산","서부산S/S 345kV CB 7100","서부산S/S 345kV #7100 GIS 차단기동작시험","서부산S/S 345kV #7100 GIS 차단기동작시험","2020-10-13 10:00","2020-10-13 18:00","2020-10-13 10:00","2020-10-13 18:00","연속"]
[274,"부산울산","서부산","서부산S/S 345kV CB 7172","서부산S/S 345kV #7172 GIS 차단기동작시험","서부산S/S 345kV #7172 GIS 차단기동작시험","2020-10-15 10:00","2020-10-15 18:00","2020-10-15 10:00","2020-10-15 18:00","연속"]
[275,"부산울산","서부산","서부산S/S 345kV CB 7200","서부산S/S 345kV #7200 GIS 차단기동작시험","서부산S/S 345kV #7200 GIS 차단기동작시험","2020-10-19 10:00","2020-10-19 18:00","2020-10-19 10:00","2020-10-19 18:00","연속"]
[276,"부산울산","서부산","서부산S/S 345kV CB 7271","서부산S/S 345kV #7271 GIS 차단기동작시험","서부산S/S 345kV #7271 GIS 차단기동작시험","2020-10-20 10:00","2020-10-20 18:00","2020-10-20 10:00","2020-10-20 18:00","연속"]
[277,"부산울산","서부산","서부산S/S 345kV CB 7272","서부산S/S 345kV #7272 GIS 차단기동작시험","서부산S/S 345kV #7272 GIS 차단기동작시험","2020-10-21 10:00","2020-10-21 18:00","2020-10-21 10:00","2020-10-21 18:00","연속"]
[278,"부산울산","서부산","서부산S/S 345kV CB 7277","서부산S/S 345kV #7277 GIS 차단기동작시험","서부산S/S 345kV #7277 GIS 차단기동작시험","2020-10-22 10:00","2020-10-22 18:00","2020-10-22 10:00","2020-10-22 18:00","연속"]
[279,"부산울산","서부산","신녹산S/S 345kV CB 7271","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해-신녹산#1T/L CB(7271) 정밀점검","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[280,"부산울산","서부산","신김해신녹산#1 T/L","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해-신녹산#1T/L CB(7271) 시험가압","2020-10-08 17:00","2020-10-08 18:00","2020-10-08 17:00","2020-10-08 18:00","연속"]
[281,"부산울산","서부산","신녹산S/S 345kV CB 7200","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해#1T/L-#2M.Tr 1차 TIE CB(7200) 정밀점검","2020-10-12 09:00","2020-10-15 18:00","2020-10-12 09:00","2020-10-15 18:00","연속"]
[282,"부산울산","서부산","신김해신녹산#1 T/L","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S 신김해#1T/L-#2M.Tr 1차 TIE CB(7200) 시험가압","2020-10-15 17:00","2020-10-15 18:00","2020-10-15 17:00","2020-10-15 18:00","연속"]
[283,"부산울산","서부산","신녹산S/S 345kV CB 7272","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S #2M.Tr 1차 CB(7272) 정밀점검","2020-10-19 09:00","2020-10-22 18:00","2020-10-19 09:00","2020-10-22 18:00","연속"]
[284,"부산울산","서부산","신김해신녹산#1 T/L","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S #2M.Tr 1차 CB(7272) 시험가압","2020-10-22 17:00","2020-10-22 18:00","2020-10-22 17:00","2020-10-22 18:00","연속"]
[285,"부산울산","서부산","신녹산S/S #2 M.Tr","신녹산S/S 362kV GIS 정밀점검 공사","신녹산S/S #2M.Tr 1차 CB(7272) 시험가압","2020-10-22 17:00","2020-10-22 18:00","2020-10-22 17:00","2020-10-22 18:00","연속"]
[286,"부산울산","울산","북부산신온산 T/L","345kV 신온산S/S 용량부족 차단기 대체공사","345kV 신온산S/S 용량부족 차단기 대체공사 -345kV #2BUS 시험가압선로","2020-10-17 18:00","2020-10-18 18:00","취소","취소","연속"]
[287,"부산울산","울산","신온산S/S 345kV #2 BUS","345kV 신온산S/S 용량부족 차단기 대체공사","345kV 신온산S/S 용량부족 차단기 대체공사 -345kV #2BUS 신설 PT 및 71BAY #2BUS 63kA 모선 설치","2020-10-14 08:00","2020-10-18 18:00","취소","취소","연속"]
[288,"부산울산","울산","신온산S/S 345kV CB 7572","20-21년 변전정비회사 총액공사","- 7572 차단기 동작시험","2020-10-21 14:00","2020-10-21 18:00","2020-10-21 14:00","2020-10-21 18:00","연속"]
[289,"부산울산","울산","신온산S/S 345kV CB 7400","20-21년 변전정비회사 총액공사","- 7400 차단기 동작시험","2020-10-21 09:00","2020-10-21 14:00","2020-10-21 09:00","2020-10-21 14:00","연속"]
[290,"부산울산","울산","신온산S/S 345kV #1 BUS","345kV 신온산S/S 용량부족 차단기 대체공사","345kV 신온산S/S 용량부족 차단기 대체공사 -345kV 76BAY #1BUS 모선철거","2020-10-22 08:00","2020-10-25 18:00","취소","취소","연속"]
[291,"부산울산","울산","신온산S/S #3 M.Tr","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- 2차 GIS 정밀점검","2020-10-28 09:00","2020-10-29 18:00","2020-10-28 09:00","2020-10-29 18:00","연속"]
[292,"부산울산","울산","신온산신울산#1 T/L","345kV 신온산S/S 용량부족 차단기 대체공사","345kV 신온산S/S 용량부족 차단기 대체공사 -345kV #1BUS 시험가압선로","2020-10-24 18:00","2020-10-25 18:00","취소","취소","연속"]
[293,"부산울산","울산","신울산S/S #3 M.Tr","20-21년 변전정비회사 총액공사","- 7500,7571,6364 차단기 동작시험 - 부싱절연유 채유","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[294,"부산울산","울산","신울산S/S #1 M.Tr","20-21년 변전정비회사 총액공사","- 2차 GCB 보통점검","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[295,"부산울산","울산","신울산S/S #5 M.Tr","20-21년 변전정비회사 총액공사","- 2차 GIS 6564 차단기 동작시험","2020-10-07 09:00","2020-10-07 18:00","2020-10-07 09:00","2020-10-07 18:00","연속"]
[296,"부산울산","울산","신울산S/S #4 M.Tr","20-21년 변전정비회사 총액공사","- 7600,7672 차단기 동작시험 - 1,2차 부싱절연유 채유","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[297,"부산울산","울산","울산C/C #3 Tie-Tr","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 전 모선마감 처리 후 시험가압 1H","2020-09-23 17:00","2020-09-23 18:00","취소","취소","연속"]
[298,"부산울산","울산","울산C/C 345kV CB 7100","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS 도킹연결 작업 인접구간휴전","2020-09-24 09:00","2020-10-10 18:00","취소","취소","연속"]
[299,"부산울산","울산","울산C/C 345kV #1 BUS","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 전 모선마감처리 휴전","2020-09-22 09:00","2020-09-23 18:00","취소","취소","연속"]
[300,"부산울산","울산","울산C/C 345kV #1 BUS","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS설치 후 모선마감처리 휴전","2020-10-31 09:00","2020-11-02 18:00","2020-10-31 09:00","2020-11-02 18:00","연속"]
[301,"부산울산","울산","울산C/C 345kV CB 7A00","울산복합S/Y 345kV SW증설공사","- 345kV 울산복합-북부산#1,2T/L(7A71, 7171)용 GIS 도킹연결 작업 인접구간휴전","2020-09-24 09:00","2020-10-10 18:00","취소","취소","연속"]
[302,"부산울산","울산","울주S/S 345kV CB 7971","20-21년 변전정비회사 총액공사","- 7971 차단기 동작시험","2020-10-08 09:00","2020-10-08 14:00","2020-10-08 09:00","2020-10-08 14:00","연속"]
[303,"부산울산","울산","울주S/S 345kV CB 7900","20-21년 변전정비회사 총액공사","- 7900 차단기 동작시험","2020-10-08 14:00","2020-10-08 18:00","2020-10-08 14:00","2020-10-08 18:00","연속"]
[304,"부산울산","울산","울주S/S 345kV CB 7800","20-21년 변전정비회사 총액공사","- 7800 차단기 동작시험","2020-10-07 09:00","2020-10-07 18:00","2020-10-07 09:00","2020-10-07 18:00","연속"]
[305,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(2차)","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-17 18:00","2020-10-18 18:00","2020-10-17 18:00","2020-10-18 18:00","연속"]
[306,"경남","직할","신김해S/S 345kV CB 7171","신김해S/S 345kV 신마산-신김해#2T/L CB(7171) 전자변교체","신김해S/S 345kV 신마산-신김해#2T/L CB(7171) 전자변 교체","2020-10-21 09:30","2020-10-21 17:30","2020-10-21 09:30","2020-10-21 17:30","연속"]
[307,"경남","직할","신김해북부산#1 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 철탑설치 및 철거 : 각 2기 ○ 전력선 및 가공지선 교체 : 1.4km (93-97호) ○ 스페이서 댐퍼 교체","2020-10-16 07:00","2020-10-19 18:00","취소","취소","연속"]
[308,"경남","직할","신김해창원#1 T/L","신김해- 창원#1 T/L 송전선로 초기및 정밀점검","신김해-창원#1 송전선로 초기점검(1~7)및 정밀점검(8~53)","2020-10-12 08:00","2020-10-14 17:00","2020-10-12 08:00","2020-10-14 17:00","매일"]
[309,"경남","직할","신김해창원#1 T/L","신김해- 창원#1 T/L 송전선로 정밀점검","신김해-창원#1 송전선로 정밀점검(8~53)","2020-10-06 08:00","2020-10-08 17:00","2020-10-06 08:00","2020-10-08 17:00","매일"]
[310,"경남","직할","신김해북부산#2 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 철탑설치 및 철거 : 각 2기 ○ 전력선 및 가공지선 교체 : 1.4km (93-97호) ○ 스페이서 댐퍼 교체","2020-10-09 07:00","2020-10-12 18:00","취소","취소","연속"]
[311,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(2차)","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-10 12:00","2020-10-10 18:00","2020-10-10 12:00","2020-10-10 18:00","연속"]
[312,"경남","직할","신김해S/S 345kV CB 7271","신김해S/S 345kV 신마산-신김해#1T/L CB(7271) 전자변교체","신김해S/S 345kV 신마산-신김해#1T/L CB(7271) 전자변 교체","2020-10-22 09:30","2020-10-22 17:30","2020-10-22 09:30","2020-10-22 17:30","연속"]
[313,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(2차)","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-23 18:00","2020-10-25 18:00","2020-10-23 18:00","2020-10-25 18:00","연속"]
[314,"경남","직할","신김해S/S #2 M.Tr","신김해S/S 154kV 장기사용GIS 교체공사(3차)","신김해S/S 154kV 장기사용GIS 교체공사(3차) 대상 : 신김해-장유#2T/L, #2BUS TIE, #2BUS PT, ES","2020-10-31 12:00","2020-10-31 18:00","2020-10-31 12:00","2020-10-31 18:00","연속"]
[315,"경남","직할","창원삼천포TP#2 T/L","창원-삼천포#2 T/L 송전선로 초기및 정밀점검","창원-삼천포#2 송전선로 초기점검(184-189)및 정밀점검(103~183)","2020-10-13 08:00","2020-10-23 17:00","2020-10-13 08:00","2020-10-23 17:00","연속"]
[316,"경남","직할","창원S/S #1 M.Tr","창원S/S 345kV #1M.Tr 1, 2, 3차 GIS 조작시험","창원S/S 345kV #1M.Tr 1, 2, 3차 GIS 조작시험","2020-10-12 09:30","2020-10-12 17:30","2020-10-12 09:30","2020-10-12 17:30","연속"]
[317,"경남","직할","신김해창원#2 T/L","신김해- 창원#2 T/L 송전선로 정밀점검","신김해-창원#2 송전선로 정밀점검(53)","2020-10-05 08:00","2020-10-05 17:00","2020-10-05 08:00","2020-10-05 17:00","매일"]
[318,"경남","진주","의령산청양수#2 T/L","산청P/P 의령-산청P/P#2T/L - #1M.Tr 1차 GIS 조작시험","산청P/P 의령-산청P/P#2T/L - #1M.Tr 1차 GIS 조작시험 - 병행 : 1. 산청P/P 의령-산청P/P#2T/L PT 및 LA 보통점검 2. 의령S/S 의령-산청P/P#2T/L -#1M.Tr 1차 GIS 보통점검 3. 의령S/S 의령-산청P/P#2T/L PT 및 LA 보통점검","2020-10-07 10:00","2020-10-08 18:00","2020-10-07 10:00","2020-10-08 18:00","연속"]
[319,"경남","진주","의령산청양수#1 T/L","산청P/P 의령-산청양수#1T/L-#1, 2M.Tr 1차 CB 조작시험","산청P/P 의령-산청양수#1T/L - #1, 2M.Tr 1차 CB 조작시험 등 병행 : 의령, 산청P/P 의령-산청양수#1T/L PT, LA 보통점검","2020-10-05 10:00","2020-10-06 18:00","2020-10-05 10:00","2020-10-06 18:00","연속"]
[320,"경남","진주","의령S/S #1 M.Tr","의령S/S #1M.Tr 2차 GIS 및 3차 VCB 조작시험","의령S/S #1M.Tr 2차 GIS 및 3차 VCB 조작시험","2020-10-07 10:00","2020-10-07 18:00","2020-10-07 10:00","2020-10-07 18:00","연속"]
[321,"경남","진주","하동T/P 345kV CB 7171","하동T/P #1M.Tr 1차 및 TIE CB 보통점검","하동T/P #1M.Tr 1차(7172) 및 #1M.Tr - 의령-하동화력#1T/L TIE CB(7100) 보통점검","2020-10-13 10:00","2020-10-13 16:00","2020-10-22 10:00","2020-10-22 16:00","연속"]
[322,"경남","진주","광양하동TP#2 T/L","하동T/P 광양-하동TP#2T/L-#6M.Tr Bay B/F PNL 대체","하동T/P 광양-하동TP#2T/L-#6M.Tr Bay B/F PNL 대체 - 병행 : 광양-하동TP#2T/L GIS(7671) 보통점검 및 PT 보통점검","2020-10-14 10:00","2020-10-20 18:00","2020-10-14 10:00","2020-10-20 18:00","연속"]
[323,"경남","진주","하동T/P 345kV CB 7372","하동T/P #3M.Tr 1차 및 TIE CB 보통점검","하동T/P #3M.Tr 1차(7372) 및 #3M.Tr - 광양-하동화력#1T/L TIE CB(7300) 보통점검","2020-10-15 10:00","2020-10-15 16:00","2020-10-15 10:00","2020-10-15 16:00","연속"]
[324,"경남","진주","하동T/P 345kV CB 7371","하동T/P #3M.Tr 1차 및 TIE CB 보통점검","하동T/P #3M.Tr 1차(7372) 및 #3M.Tr - 광양-하동화력#1T/L TIE CB(7300) 보통점검","2020-10-16 10:00","2020-10-16 16:00","2020-10-16 10:00","2020-10-16 16:00","연속"]
[325,"경남","진주","의령하동화력#2 T/L","하동T/P 의령-하동TP#2T/L-#5M.Tr Bay B/F PNL 대체","하동T/P 의령-하동TP#2T/L-#5M.Tr Bay B/F PNL 대체 - 병행 : 의령-하동TP#2T/L GIS(7571) 보통점검 및 PT 보통점검","2020-10-22 10:00","2020-10-29 18:00","2020-10-26 10:00","2020-10-27 18:00","연속"]
[326,"경남","진주","하동T/P 345kV CB 7572","하동T/P #5M.Tr 1차 및 TIE CB 보통점검","하동T/P #5M.Tr 1차(7572) 및 #5M.Tr - 의령-하동화력#2T/L TIE CB(7500) 보통점검","2020-10-26 10:00","2020-10-26 16:00","취소","취소","연속"]
[327,"경남","진주","하동T/P 345kV CB 7572","하동T/P #5M.Tr 1차 및 TIE CB 보통점검","하동T/P #5M.Tr 1차(7572) 및 #5M.Tr - 의령-하동화력#2T/L TIE CB(7500) 보통점검","2020-10-27 10:00","2020-10-27 16:00","취소","취소","연속"]
[328,"경남","진주","하동T/P 345kV CB 7172","하동T/P #1M.Tr 1차 및 TIE CB 보통점검","하동T/P #1M.Tr 1차(7172) 및 #1M.Tr - 의령-하동화력#1T/L TIE CB(7100) 보통점검","2020-10-12 10:00","2020-10-12 16:00","2020-10-21 10:00","2020-10-21 16:00","연속"]
[329,"경남","통영","고성하이T/P 345kV CB 7272","고성하이S/Y 7272 GIS 초기점검","1. 고성하이S/Y 7272 GIS 초기점검","2020-10-29 10:00","2020-10-29 18:00","취소","취소","연속"]
[330,"경남","통영","고성하이T/P 345kV CB 7171","고성하이S/Y 7171 GIS 초기점검","1. 고성하이S/Y 7171 GIS 초기점검","2020-10-05 10:00","2020-10-05 18:00","2020-10-05 10:00","2020-10-05 18:00","연속"]
[331,"경남","통영","고성하이T/P 345kV CB 7271","고성하이S/Y 7271 GIS 초기점검","1. 고성하이S/Y 7271 GIS 초기점검","2020-10-06 10:00","2020-10-06 18:00","2020-10-06 10:00","2020-10-06 18:00","연속"]
[332,"경남","통영","고성하이T/P 345kV CB 7200","고성하이S/Y 7200 GIS 초기점검","1. 고성하이S/Y 7200 GIS 초기점검","2020-10-07 10:00","2020-10-07 18:00","2020-10-07 10:00","2020-10-07 18:00","연속"]
[333,"경남","통영","창원삼천포TP#1 T/L","345kV 창원-삼천포화력#1T/L 전선교체공사","345kV 창원-삼천포화력#1T/L 전선교체공사(87~91호)","2020-10-24 08:00","2020-11-04 18:00","2020-10-24 08:00","2020-11-04 18:00","연속"]
[334,"경남","통영","신고성S/S #2 M.Tr","신고성S/S #2M.Tr 보통점검 등 4건","1. 신고성S/S #2M.Tr 보통점검 2. 신고성S/S #2M.Tr 1,2차 부싱 절연유 채유, 1,2,3차 LA 보통점검 3. 신GIS 7372 보통점검, 2차 GIS 보통점검 및 전자변 교체 4. #5S.Tr 보통점검, VCB 조작시험","2020-10-12 10:00","2020-10-14 18:00","2020-10-12 10:00","2020-10-14 18:00","연속"]
[335,"경남","통영","신고성S/S #1 M.Tr","신고성S/S #1M.Tr 보통점검 등 4건","1. 신고성S/S #1M.Tr 보통점검 2. 신고성S/S #1M.Tr 1,2차 부싱 절연유 채유, 1,2,3차 LA 보통점검 3. 2차 GIS 보통점검 및 전자변 교체, #1-1,2 Sh.R 보통점검 4. #4S.Tr 보통점검, VCB 조작시험","2020-10-19 10:00","2020-10-22 18:00","2020-10-19 10:00","2020-10-22 18:00","연속"]
[336,"경남","통영","신고성S/S 345kV CB 7171","신고성S/S 7171 GIS 조작시험","1. 신고성S/S 7171 GIS 조작시험","2020-10-30 10:00","2020-10-30 18:00","2020-10-30 10:00","2020-10-30 18:00","연속"]
[337,"경남","함안","신마산S/S #1 M.Tr","신마산S/S 345kV #1 M.Tr 보통점검 외","신마산S/S 345kV #1 M.Tr 보통점검 외","2020-10-19 09:00","2020-10-21 18:00","2020-10-19 09:00","2020-10-21 18:00","연속"]
[338,"경남","함안","신마산S/S #4 M.Tr","신마산S/S 345kV #4 M.Tr 보통점검 외","신마산S/S 345kV #4 M.Tr 보통점검 외","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[339,"경남","함안","신마산S/S #2 M.Tr","신마산S/S 345kV #2 M.Tr 보통점검 외","신마산S/S 345kV #2 M.Tr 보통점검 외","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","연속"]
[340,"경남","함안","신마산S/S #3 M.Tr","신마산S/S 345kV #3 M.Tr 보통점검 외","신마산S/S 345kV #3 M.Tr 보통점검 외","2020-10-15 09:00","2020-10-17 18:00","2020-10-15 09:00","2020-10-17 18:00","연속"]
[341,"대전충남","보령","보령T/P 345kV #77BUS","송전선로 정밀점검 및 GIS 보통점검","345kV 보령-보령복합(연락) #2 T/L 정밀점검 및 GIS 78Bay & #2 Bus 보통점검","2020-10-12 09:00","2020-10-16 18:00","2020-11-23 09:00","2020-11-27 17:00","연속"]
[342,"대전충남","보령","보령TP보령CC#2 T/L","송전선로 정밀점검 및 GIS 보통점검","345kV 보령-보령복합(연락) #2 T/L 정밀점검 및 GIS 78Bay & #2 Bus 보통점검","2020-10-12 09:00","2020-10-16 18:00","2020-11-23 09:00","2020-11-27 17:00","연속"]
[343,"대구","월성","월성N/P #4호기 주변압기 CB (7700, 7772)","월성4호기 17차 O/H 중 발전기 링크 조립 및 대기 * 조작차단기 : CB 7700, 7772","○ 계통연결전 발전기 링크 조립 및 대기","2020-10-05 08:00","2020-10-09 11:00","2020-10-05 08:00","2020-10-09 11:00","연속"]
[344,"대구","월성","월성N/P #2 기동용변압기 CB (7472, 7400)","월성 2호기 제19차 계획예방정비 관련 기동용변압기 점검 * 조작차단기 : CB7472,7400","기동용변압기 일반점검, 기동용변압기 보호계전기 정기시험(차단기 연동시험 포함)","2020-10-21 09:00","2020-10-29 18:00","2020-10-21 09:00","2020-10-29 18:00","연속"]
[345,"강원",null,"삼척G/P1호기 주변압기 CB (7700,7772)","계획예방정비","계획예방정비","2020-10-05 10:00","2020-12-11 10:00","2020-10-05 10:00","2020-12-11 10:00","연속"]
[346,"광주전남",null,"광양광양제철#1T/L","송전선로 금구류 Re-bolting 작업","송전선로 금구류 Re-bolting 작업","2020-10-12 08:00","2020-10-16 17:00","2020-10-12 08:00","2020-10-16 17:00","연속"]
[347,"광주전남",null,"광양광양제철#2T/L","송전선로 금구류 Re-bolting 작업","송전선로 금구류 Re-bolting 작업","2020-10-19 08:00","2020-10-23 17:00","2020-10-19 08:00","2020-10-23 17:00","연속"]
[348,"전북","군산","군산S/S #3 M.Tr","345kV 군산S/S Sh.R 설치공사 (시험가압)","***무부하가압 선로(#75BUS) 345kV 군산S/S Sh.R 설치공사","2020-10-15 09:00","2020-10-16 18:00","2020-10-15 09:00","2020-10-16 18:00","연속"]
[349,"전북",null,"무주양수1,2호기 주변압기 CB(7100,7200)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-10-14 12:00","2020-10-14 14:00","2020-10-14 12:00","2020-10-14 14:00","연속"]
[350,"전북",null,"무주양수1,2호기 주변압기 CB(7100,7200)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-10-28 12:00","2020-10-28 14:00","2020-10-28 12:00","2020-10-28 14:00","연속"]
[351,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7200,7172,7271)","자체기동발전기 사전시험","자체기동발전기 사전시험","2020-10-13 12:00","2020-10-13 14:00","2020-10-13 12:00","2020-10-13 14:00","연속"]
[352,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7200,7172,7271)","자체기동발전기 사전시험","자체기동발전기 사전시험","2020-10-15 12:00","2020-10-15 14:00","2020-10-15 12:00","2020-10-15 14:00","연속"]
[353,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7200,7172,7271)","자체기동발전기 사전시험","자체기동발전기 사전시험","2020-10-16 12:00","2020-10-16 14:00","2020-10-16 12:00","2020-10-16 14:00","연속"]
[354,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7200,7172,7271)","자체기동발전기 정기시험","자체기동발전기 정기시험","2020-10-22 14:00","2020-10-22 16:00","2020-10-22 14:00","2020-10-22 16:00","연속"]
[355,"경남",null,"산청양수1호기 주변압기 CB(7100,7172)","계획중간정비","계획중간정비","2020-10-17 09:00","2020-10-17 18:00","2020-10-17 09:00","2020-10-17 18:00","연속"]
[356,"강원",null,"양양양수2호기 주변압기 CB(7271,7200)","AVR DC 차단기 교체","AVR DC 차단기 교체","2020-10-13 13:00","2020-10-13 18:00","2020-10-13 13:00","2020-10-13 18:00","연속"]
[357,"강원",null,"양양양수3호기 주변압기 CB(7200,7272)","AVR DC 차단기 교체","AVR DC 차단기 교체","2020-10-14 13:00","2020-10-14 18:00","2020-10-14 13:00","2020-10-14 18:00","연속"]
[358,"강원",null,"양양양수4호기 주변압기 CB(7300,7372)","AVR DC 차단기 교체","AVR DC 차단기 교체","2020-10-15 13:00","2020-10-15 18:00","2020-10-15 13:00","2020-10-15 18:00","연속"]

{"sheet":"154송부","index":2,"n_rows":752,"n_cols":11,"rows_kept":752,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,2,3,2]]}
["2020년도 10월 휴전계획서"]
["154kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","성동","천호구의#1 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-29 14:00","2020-10-29 17:00","취소","취소","연속"]
[2,"서울","성동","군자성수 T/L","2020년 성동 변전정비회사 총액공사","170kV GIS 보통점검","2020-10-06 10:00","2020-10-06 18:00","2020-10-06 10:00","2020-10-06 18:00","연속"]
[3,"서울","성동","금오상계#1 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 40호","2020-10-15 08:00","2020-10-15 13:00","2020-10-15 08:00","2020-10-15 18:00","연속"]
[4,"서울","성동","금오상계#2 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 54호","2020-10-15 13:00","2020-10-15 18:00","2020-10-16 08:00","2020-10-16 18:00","연속"]
[5,"서울","성동","성동휘경#2 T/L","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-10-07 14:00","2020-10-07 17:30","2020-10-07 14:00","2020-10-07 17:30","연속"]
[6,"서울","성동","성동S/S 154kV CB 6200","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-10-30 11:00","2020-10-30 13:00","2020-10-30 11:00","2020-10-30 13:00","연속"]
[7,"서울","성동","성동S/S 154kV CB 6100","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-10-30 09:00","2020-10-30 11:00","2020-10-30 09:00","2020-10-30 11:00","연속"]
[8,"서울","성동","성동S/S 154kV SEC CB 65660","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-10-30 15:00","2020-10-30 17:30","2020-10-30 15:00","2020-10-30 17:30","연속"]
[9,"서울","성동","성동S/S 154kV SEC CB 60610","20년 성동P/O 변전정비회사 총액공사","차단기 동작특성 시험 - 광장S/S 154kV BUS TIE GIS 외 45BAY","2020-10-30 13:00","2020-10-30 15:00","2020-10-30 13:00","2020-10-30 15:00","연속"]
[10,"서울","성동","성수뚝도#2 T/L","'20년 성동P/O 노후 보호배전반 교체공사","성수, 뚝도S/S 154kV 성수뚝도#2T/L 보호배전반 노후대체","2020-10-19 10:00","2020-10-22 17:00","2020-10-19 10:00","2020-10-22 17:00","연속"]
[11,"서울","성동","성수뚝도#1 T/L","'20년 성동P/O 노후 보호배전반 교체공사","성수, 뚝도S/S 154kV 성수뚝도#1T/L 보호배전반 노후대체","2020-10-12 10:00","2020-10-15 17:00","2020-10-12 10:00","2020-10-15 17:00","연속"]
[12,"서울","성동","양주쌍문#2 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 38, 39호 추락방지시설 : 39호","2020-10-13 08:00","2020-10-13 18:00","2020-10-13 08:00","2020-10-13 18:00","연속"]
[13,"서울","성동","쌍문미아#1 T/L","154kV 수유분기 지중T/L 건설공사","- 구간 : 수유S/S~쌍문미아T/L 분기점 - 선종/회선수 : XLPE 1200SQ/ 2회선-0.3km","2020-10-05 09:00","2020-11-21 18:00","2020-10-05 09:00","2020-11-21 18:00","연속"]
[14,"서울","성동","양주쌍문#1 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 38, 39호 추락방지시설 : 39호","2020-10-12 08:00","2020-10-12 18:00","2020-10-12 08:00","2020-10-12 18:00","연속"]
[15,"서울","성동","용두안암#2 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-14 14:00","2020-10-14 17:00","2020-10-14 14:00","2020-10-14 17:00","연속"]
[16,"서울","성동","용두안암#1 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-14 10:00","2020-10-14 14:00","2020-10-14 10:00","2020-10-14 14:00","연속"]
[17,"서울","성동","방학창동#2 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-23 14:00","2020-10-23 17:00","2020-10-23 14:00","2020-10-23 17:00","연속"]
[18,"서울","성동","창동쌍문#1 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-22 10:00","2020-10-22 14:00","2020-10-22 10:00","2020-10-22 14:00","연속"]
[19,"서울","성동","창동쌍문#2 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-22 14:00","2020-10-22 17:00","2020-10-22 14:00","2020-10-22 17:00","연속"]
[20,"서울","성동","방학창동#1 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-23 10:00","2020-10-23 14:00","2020-10-23 10:00","2020-10-23 14:00","연속"]
[21,"서울","성동","창동돈암 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-26 10:00","2020-10-26 14:00","취소","취소","연속"]
[22,"서울","성동","창동S/S 154kV CB 6100","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-26 14:00","2020-10-26 17:00","취소","취소","연속"]
[23,"서울","성동","군자화양#2 T/L","20년 성동PO 변전정비회사 총액공사","장기미동작 차단기 동작시험","2020-10-28 10:00","2020-10-28 14:00","취소","취소","연속"]
[24,"서울","중부","순화동빙고 T/L","154kV 순화동빙고T/L 케이블 교체공사","■ 선로명 : 154kV 순화동빙고T/L ■ 선종 및 길이 : 154kV OF 1,200㎟ × 1회선 - 2.14km → XLPE 1,200㎟ × 1회선 - 2.14km ■ 포설 및 접속 : 포설 7구간, 접속 8개소 (중간7개소, 종단1개소)","2020-10-05 09:00","2020-12-18 18:00","2020-10-12 09:00","2020-12-18 18:00","연속"]
[25,"서울","중부","상암등촌#1 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 1, 4호 추락방지시설 : 1, 2, 4, 5, 6호","2020-10-27 08:00","2020-10-28 18:00","취소","취소","연속"]
[26,"서울","중부","능곡상암#2 T/L","(주)세니온 내부부품 교체","(주)세니온 내부부품 교체","2020-10-21 15:00","2020-10-21 17:00","2020-10-21 15:00","2020-10-21 17:00","연속"]
[27,"서울","중부","능곡상암#1 T/L","(주)세니온 내부부품 교체","(주)세니온 내부부품 교체","2020-10-21 13:00","2020-10-21 15:00","2020-10-21 13:00","2020-10-21 15:00","연속"]
[28,"서울","중부","상암등촌#2 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","불량애자 교체 : 1, 7호 추락방지시설 : 1, 2, 4, 5, 6호","2020-10-29 08:00","2020-10-30 18:00","취소","취소","연속"]
[29,"서울","중부","지축현저#1 T/L","2020~2021 서울본부 가공송전정비회사 총액공사","추락방지시설 : 4, 4.1호","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[30,"서울","직할","중앙서소문 T/L","20년 직할 변전협력 총액공사","GIS 조작시험","2020-10-07 10:00","2020-10-07 18:00","2020-10-07 10:00","2020-10-07 18:00","연속"]
[31,"남서울","강남","사당봉천#1 T/L","170kV GIS 개폐타임측정-변전협력","사당-봉천#1/L GIS 개폐타임 측정","2020-10-30 15:00","2020-10-30 18:00","2020-10-30 15:00","2020-10-30 18:00","연속"]
[32,"남서울","강남","사당신림 T/L","170kV GIS 보통점검-변전협력","170kV 사당-신림T/L GIS 보통점검(사당S/S)","2020-10-30 09:00","2020-10-30 15:00","2020-10-30 09:00","2020-10-30 15:00","연속"]
[33,"남서울","강남","신양재역삼#3 T/L","154kV 신양재-역삼#3T/L 접속함 누유복구 공사","접속함 누유발생 관련 복구 공사","2020-10-12 09:00","2020-10-23 18:00","2020-10-12 09:00","2020-10-23 18:00","연속"]
[34,"남서울","강남","역삼S/S 154kV #1 BUS","154kV 역삼S/S 가스변압기 대체공사","○ 154kV 난연유 변압기 철거(154/23kV, 15/20MVA) × 12대 ○ 154kV 가스변압기 설치(154/23kV, 60MVA) × 4Bank ○ 154kV GIB 개조 및 LA 설치 × 1식 ○ 수냉각설비 개조 및 기타부대공사 × 1식","2020-10-28 09:00","2020-10-29 18:00","2020-10-28 09:00","2020-10-29 18:00","연속"]
[35,"남서울","동서울","염곡개포#2 T/L","154kv염곡-개포T/L 지장이설","염곡-개포T/L 지장이설 1. 구 간 및 선종 : M/H#4~#5 약 450m (OF2000) 2회선 2. 공사기간 (케이블) 20년 08월 ~ 20년 12월 3. 이설 비용 : 서초구청 4. 시공업체 : LS전선 5. 특이사항 : 기존 관로경과지에 전력구 신설","2020-10-05 09:00","2020-11-27 18:00","2020-10-05 09:00","2020-11-27 18:00","연속"]
[36,"남서울","동서울","동서울서종#1 T/L","20~21년 동서울전력지사 가공송전정비회사 총액공사","철탑 추락방지시설 설치공사","2020-10-15 08:00","2020-10-15 18:00","2020-10-15 08:00","2020-10-15 18:00","연속"]
[37,"남서울","동서울","동서울신장#1 T/L","154kV 동서울-강동T/L 등 5개 T/L 지중화(이설)공사","154kV 동서울-강동T/L No.1~4 가철탑 공사(요청자 한국도로공사 시행)","2020-10-09 09:00","2020-10-18 18:00","2020-10-23 09:00","2020-11-01 18:00","연속"]
[38,"남서울","동서울","동서울서종#2 T/L","20~21년 동서울전력지사 가공송전정비회사 총액공사","철탑 추락방지시설 설치공사","2020-10-16 08:00","2020-10-16 18:00","2020-10-16 08:00","2020-10-16 18:00","연속"]
[39,"남서울","동서울","동서울S/S 154kV #60 BUS","동서울S/S 345kV 노후 주변압기 교체공사","○ 345kV M.Tr 7대 교체 ○ 기타 부대작업 1식","2020-10-27 13:00","2020-10-27 16:00","2020-10-27 13:00","2020-10-27 16:00","연속"]
[40,"남서울","동서울","동서울신장#2 T/L","154kV 동서울-강동T/L 등 5개 T/L 지중화(이설)공사","154kV 동서울-강동T/L No.1~4 가철탑 공사(요청자 한국도로공사 시행)","2020-10-19 09:00","2020-10-25 18:00","2020-11-02 09:00","2020-11-08 18:00","연속"]
[41,"남서울","동서울","동서울송파#1 T/L","154kV 동서울-송파#1T/L 급유설비 정비공사","거여C/H 압력유조내 절연유 교체 등 급유설비 정비","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[42,"남서울","동서울","상일S/S 154kV #1 BUS","154kV 상일S/S #4M.Tr 증설공사","- 170kV GIS * 1CCT - 154kV M.Tr * 1BANK - 25.8kV GIS * 4CCT","2020-10-17 09:00","2020-10-18 18:00","취소","취소","연속"]
[43,"남서울","동서울","강동상일#1 T/L","154kV 상일S/S #4M.Tr 증설공사","- 170kV GIS * 1CCT - 154kV M.Tr * 1BANK - 25.8kV GIS * 4CCT","2020-10-17 09:00","2020-10-18 18:00","취소","취소","연속"]
[44,"남서울","동서울","풍납석촌#2 T/L","송전선로 보호반 교체공사","송전선로 보호반 교체공사","2020-10-26 09:00","2020-10-28 18:00","취소","취소","연속"]
[45,"남서울","동서울","풍납석촌#1 T/L","송전선로 보호반 교체공사","송전선로 보호반 교체공사","2020-10-19 09:00","2020-10-21 18:00","취소","취소","연속"]
[46,"남서울","영등포","가양등촌#1 T/L","154kV 가양S/S 인출전력구 케이블 선종교체공사","가양S/S 인출전력구 케이블 선종교체공사 구간 : 가양S/S EBG ~ J/B#1","2020-10-27 09:00","2020-12-15 18:00","취소","취소","연속"]
[47,"남서울","영등포","신광명광명#1 T/L","광명S/S 170kV GIS 2DS 내부 점검","- 170kV GIS #2 DS 내부 과열발생 관련 내부 점검","2020-10-09 09:00","2020-10-10 18:00","취소","취소","연속"]
[48,"남서울","영등포","신광명광명#2 T/L","광명S/S 170kV GIS 2DS 내부점검","- 170kV GIS #2DS 과열발생 관련 내부 점검","2020-10-09 09:00","2020-10-10 18:00","취소","취소","연속"]
[49,"남서울","영등포","영등포구로#1 T/L","구로S/S 170kV GIS 조작시험","- 영등포-구로#1T/L GIS 조작시험 - 송전운영부 병행작업 시행","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[50,"남서울","영등포","영등포구로#2 T/L","구로S/S 170kV GIS 조작시험","- 영등포-구로#2T/L GIS 조작시험 - 송전운영부 병행작업 시행","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[51,"남서울","영등포","대방신길#2 T/L","154kV 대방인출전력구 OF케이블 선종교체공사","대방 인출전력구 내 154kV 대방-신길#2T/L 선종교체 공사 - 구간 : 대방S/S~J/B#38 - 교체전 : OF 1200, 교체후 : XLPE 1200","2020-10-31 09:00","2020-12-04 18:00","2020-10-31 09:00","2020-12-04 18:00","연속"]
[52,"남서울","영등포","대방S/S 154kV #1 BUS","154kV 대방인출전력구 OF케이블 선종교체공사","154kV 신길인출전력구 내 154kV 대방-신길#2T/L 선종교체공사 가압 전 상시험 확인","2020-10-28 12:00","2020-10-28 14:00","2020-10-28 12:00","2020-10-28 14:00","연속"]
[53,"남서울","영등포","신광명소래 T/L","154kV 신광명-소래T/L No.19~21 안전이격 확보공사","철탑 : 이설 2기, 인클로징 1기(산형강 신설 총 3기) 전력선 : ACSR × 330㎟ × S (경간 : 1.031km)","2020-10-26 09:00","2020-11-04 18:00","2020-10-26 09:00","2020-11-04 18:00","연속"]
[54,"남서울","영등포","양천S/S 154kV #2 BUS","154kV 양평-양천T/L 선종교체공사","○ 위 치 : 양평, 양천S/S 및 목동공동구, 맨홀·전력구 ○ 선 로 명 : 154kV 양평-양천#1T/L ○ 구 간 : 양평S/S ∼양천S/S ○ 주요공종 - 케이블 철거구간 : OF 1200㎟ × 10구간× 1C(B)×2.46km) - 케이블 포설구간 : XLPE 1200㎟ × 5구간 ×1C(B)×1.474km (관로 1공3조), XLPE 2000㎟ × 3구간 ×1C(S)×1km(공동구,전력구)","2020-10-19 10:00","2020-10-19 10:05","2020-10-19 10:00","2020-10-19 11:00","연속"]
[55,"남서울","영등포","온수소래 T/L","154kV 신광명-소래T/L No.19~21 안전이격 확보공사","철탑 : 이설 2기, 인클로징 1기(산형강 신설 총 3기) 전력선 : ACSR × 330㎟ × S (경간 : 1.031km)","2020-10-26 09:00","2020-11-04 18:00","2020-10-26 09:00","2020-11-04 18:00","연속"]
[56,"남서울","영등포","천왕오류#1 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험","2020-10-02 09:00","2020-10-03 18:00","2020-10-02 09:00","2020-10-03 18:00","연속"]
[57,"남서울","영등포","천왕오류#2 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험","2020-10-09 09:00","2020-10-10 18:00","취소","취소","연속"]
[58,"남서울","영등포","천왕구로#2 T/L","154kV 천왕-구로,오류T/L 지장송전선로 이설공사","○ 위 치 : 광명시 광명동 776-16일원 ○ 선 로 명 : 154kV 천왕-구로#2T/L ○ 구 간 : 천왕S/S S/J M/H#1 ∼M/H#3호 구간중 121m","2020-10-23 09:00","2020-11-24 18:00","2020-10-23 09:00","2020-11-24 18:00","연속"]
[59,"남서울","영등포","중동화곡#1 T/L","154kV 고강-화곡(증) 지중T/L 건설공사","XLPE 2000/1200㎟ 1C-2.4km","2020-10-31 14:00","2020-11-01 15:00","취소","취소","연속"]
[60,"남서울","영등포","화곡S/S 154kV #1 BUS","154kV 고강-화곡(증) 지중T/L 건설공사","XLPE 2000/1200㎟ 1C-2.4km","2020-10-31 14:00","2020-10-31 15:00","취소","취소","연속"]
[61,"남서울","영등포","화곡S/S 154kV #2 BUS","154kV 고강-화곡(증) 지중T/L 건설공사","XLPE 2000/1200㎟ 1C-2.4km","2020-10-31 15:00","2020-11-01 15:00","취소","취소","연속"]
[62,"남서울","영등포","화곡마곡#1 T/L","화곡S/S 화곡-마곡#1T/L 43PDA 교체","-화곡S/S 화곡-마곡#1T/L 43PDA 교체","2020-10-30 09:00","2020-10-30 18:00","취소","취소","연속"]
[63,"남서울","직할","노들노량진 T/L","OF케이블 절연유 채유작업(노들-노량진T/L)","절연열화 확인을 위한 절연유 채유 급유구간 및 채유장소 - J/B#9-1 ~ 노량진 SJ : J/B#9-1, 노량진 SJ - 노량진 SJ ~ 노량진 EBG : 노량진 SJ, 노량진 EBG","2020-10-07 09:00","2020-10-07 18:00","2020-10-17 09:00","2020-10-17 18:00","연속"]
[64,"남서울","직할","영등포노량진 T/L","170kV GIS 에어누기보수 작업","170kV GIS 에어누기보수 작업","2020-10-08 10:00","2020-10-08 18:00","2020-10-08 10:00","2020-10-08 18:00","연속"]
[65,"남서울","직할","영등포노들 T/L","170kV GIS 보통점검","영등포,노들 170kV GIS 보통점검","2020-10-13 10:00","2020-10-13 18:00","2020-10-24 09:00","2020-10-24 18:00","연속"]
[66,"남서울","직할","신길S/S 154kV CB 6100","신길S/S 23kV GIS 증설 관련 계통 통합 ","신길S/S 23kV GIS 증설 관련 계통 통합 ","2020-10-12 08:00","2020-10-16 18:00","2020-10-12 08:00","2020-10-16 18:00","연속"]
[67,"남서울","영등포","구로S/S 154kV CB 6100","구로S/S 종합예방진단시스템 설치공사 ","ㅇ구로S/S 주변압기 부싱진단장치 설치 ㅇ주변압기 OLTC 센서 설치 및 시험 ","2020-10-12 08:00","2020-10-22 18:00","2020-10-12 08:00","2020-10-22 18:00","연속"]
[68,"인천","직할","계양원창 T/L","계양S/S 계양원창T/L 170kV GIS 조작시험","계양S/S 계양원창T/L 170kV GIS 조작시험","2020-10-08 09:30","2020-10-08 18:00","2020-10-08 09:30","2020-10-08 18:00","연속"]
[69,"인천","부평","송월남인천#2T/L","변전소 인출구간 OF 선종교체 공사","OF케이블 노후화에 따른 설비교체","2020-10-05 09:00","2020-11-10 18:00","2020-10-05 09:00","2020-11-10 18:00","연속"]
[70,"인천","시흥","서시화S/S 154kV CB 6100","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사 - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-05 07:30","2020-10-30 18:00","2020-10-05 07:30","2020-10-30 18:00","연속"]
[71,"인천","시흥","북시화서시화#1 T/L","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사 - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-05 07:30","2020-10-30 18:00","2020-10-05 07:30","2020-10-30 18:00","연속"]
[72,"인천","부평","신가좌인천#1 T/L","신가좌S/S 신가좌인천#1T/L 보호반 교체공사","신가좌S/S 신가좌인천#1T/L 보호반 교체공사","2020-10-05 09:00","2020-10-08 18:00","취소","취소","연속"]
[73,"인천","부평","인천C/C 154kV CB 6200","인천복합S/Y 6200 GIS 정밀점검 공사","인천복합S/Y 6200 GIS 정밀점검 공사","2020-10-05 09:00","2020-10-07 18:00","2020-10-05 09:00","2020-10-07 18:00","연속"]
[74,"인천","시흥","신시흥#1S/S 154kV CB 6100","신시흥#1S/S 154kV 6100 BUSTIE GIS정밀점검","신시흥#1S/S 154kV 6100 BUSTIE GIS정밀점검","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[75,"인천","김포","왕길양촌#2 T/L","기중종단접속함(EBA) PD진단센서 및 집합반 설치공사","기중종단접속함(EBA) PD진단센서 및 집합반 설치공사 - 대상 : 왕길-양촌#2T/L 왕길-양촌#1,2C/H 12상 - 내용 : PD센서 설치 및 케이블 포설, 집합반 설치","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[76,"인천","김포","영종경서 T/L","경서S/S 154kV 영종-경서T/L GIS 조작시험","경서S/S 154kV 영종-경서T/L GIS 조작시험(전자변 교체 병행)","2020-10-05 10:00","2020-10-05 18:00","2020-10-05 10:00","2020-10-05 18:00","연속"]
[77,"인천","직할","신부평S/S 154kV CB 6200","신부평S/S 6200 BUS TIE 170kV GIS 조작시험","신부평S/S 6200 BUS TIE 170kV GIS 조작시험","2020-10-05 14:00","2020-10-05 18:00","2020-10-05 14:00","2020-10-05 18:00","연속"]
[78,"인천","직할","부천S/S 154kV CB 6100","부천S/S 6100 BUS TIE 170kV GIS 보통점검","부천S/S 6100 BUS TIE 170kV GIS 보통점검","2020-10-06 09:30","2020-10-06 18:00","2020-10-06 09:30","2020-10-06 18:00","연속"]
[79,"인천","직할","신부평S/S 154kV SEC CB 60610","신부평S/S 60-61 BUS SEC 170kV GIS 보통점검","신부평S/S 60-61 BUS SEC 170kV GIS 보통점검","2020-10-06 09:30","2020-10-06 14:00","2020-10-06 09:30","2020-10-06 14:00","연속"]
[80,"인천","부평","관교만수#1 T/L","병행지선 설치구간 선로정수 측정","병행지선 설치구간 선로정수 측정 공사구간 : JB6~JB7","2020-10-06 10:00","2020-10-06 14:00","2020-10-06 10:00","2020-10-06 14:00","연속"]
[81,"인천","직할","신부평S/S 154kV SEC CB 65660","신부평S/S 65-66 BUS SEC 170kV GIS 보통점검","신부평S/S 65-66 BUS SEC 170kV GIS 보통점검","2020-10-06 14:00","2020-10-06 18:00","2020-10-06 14:00","2020-10-06 18:00","연속"]
[82,"인천","시흥","신시흥#1S/S 154kV SEC CB 60610","신시흥#1S/S 154kV 6100 GIS정밀무부하(60-61휴전)","신시흥#1S/S 154kV 6100 GIS정밀무부하(60-61휴전)","2020-10-06 16:00","2020-10-06 18:00","2020-10-06 16:00","2020-10-06 18:00","연속"]
[83,"인천","시흥","신시흥#1S/S 154kV SEC CB 65660","신시흥#1S/S 154kV 6100 GIS정밀무부하(65-66휴전)","신시흥#1S/S 154kV 6100 GIS정밀무부하(65-66휴전)","2020-10-06 16:00","2020-10-06 18:00","2020-10-06 16:00","2020-10-06 18:00","연속"]
[84,"인천","직할","신부평도당#2 T/L","도당S/S 신부평도당#2T/L 170kV GIS 초기점검","도당S/S 신부평도당#2T/L 170kV GIS 초기점검","2020-10-07 09:30","2020-10-07 18:00","취소","취소","연속"]
[85,"인천","직할","부천신정#1 T/L","부천S/S 부천신정#1T/L 170kV GIS 보통점검","부천S/S 부천신정#1T/L 170kV GIS 보통점검","2020-10-07 09:30","2020-10-07 14:00","취소","취소","연속"]
[86,"인천","부평","인천T/P 154kV #66 BUS","인천복합S/Y 6200 GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 6200 GIS 정밀점검 관련 무부하 가압용","2020-10-07 13:00","2020-10-07 18:00","2020-10-07 13:00","2020-10-07 18:00","연속"]
[87,"인천","부평","인천CC북인천#1 T/L","인천복합S/Y 6200 GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 6200 GIS 정밀점검 관련 무부하 가압용","2020-10-07 13:00","2020-10-07 18:00","2020-10-07 13:00","2020-10-07 18:00","연속"]
[88,"인천","직할","부천신정#2 T/L","부천S/S 부천신정#2T/L 170kV GIS 보통점검","부천S/S 부천신정#2T/L 170kV GIS 보통점검","2020-10-07 14:00","2020-10-07 18:00","취소","취소","연속"]
[89,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사(#65BUS 무부하 및 BUS-TIE 대용) - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-08 18:00","2020-10-09 09:00","2020-10-08 18:00","2020-10-09 09:00","연속"]
[90,"인천","직할","계양북인천 T/L","154kV계양-북인천T/L 정밀점검","154kV계양-북인천T/L 정밀점검","2020-10-12 09:30","2020-10-15 18:00","2020-10-12 09:30","2020-10-15 18:00","연속"]
[91,"인천","시흥","도림오봉#1 T/L","오봉S/S 154kV 도림오봉#1T/L GIS보통점검","오봉S/S 154kV 도림오봉#1T/L GIS보통점검","2020-10-12 10:00","2020-10-12 18:00","2020-10-12 10:00","2020-10-12 18:00","연속"]
[92,"인천","직할","부흥부개#1 T/L","154kV 부흥-부개#1T/L 병행지선 설치관련 선로정수 측정","154kV 부흥-부개#1T/L 선로정수 측정 (계통시험파트)","2020-10-12 10:00","2020-10-12 14:00","2020-10-12 10:00","2020-10-12 14:00","연속"]
[93,"인천","직할","부흥부개#2 T/L","154kV 부흥-부개#2T/L 병행지선 설치관련 선로정수 측정","154kV 부흥-부개#2T/L 선로정수 측정 (계통시험파트)","2020-10-12 14:00","2020-10-12 18:00","2020-10-12 14:00","2020-10-12 18:00","연속"]
[94,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사(#60BUS 무부하 및 BUS-TIE 대용) - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-12 18:00","2020-10-13 07:30","2020-10-12 18:00","2020-10-13 07:30","연속"]
[95,"인천","김포","신김포양곡#2 T/L","양곡S/S 154kV 신김포-양곡#2T/L GIS 조작시험","양곡S/S 154kV 신김포-양곡#2T/L GIS 조작시험(전자변 교체 병행)","2020-10-13 10:00","2020-10-13 18:00","2020-10-13 10:00","2020-10-13 18:00","연속"]
[96,"인천","시흥","도림오봉#2 T/L","오봉S/S 154kV 도림오봉#2T/L GIS보통점검","오봉S/S 154kV 도림오봉#2T/L GIS보통점검","2020-10-13 10:00","2020-10-13 18:00","2020-10-13 10:00","2020-10-13 18:00","연속"]
[97,"인천","직할","부천원미#1 T/L","154kV 부천-원미#1T/L 병행지선 설치관련 선로정수 측정","154kV 부천-원미#1T/L 선로정수 측정 (계통시험파트)","2020-10-13 10:00","2020-10-13 14:00","2020-10-13 10:00","2020-10-13 14:00","연속"]
[98,"인천","직할","부천원미#2 T/L","154kV 부천-원미#2T/L 병행지선 설치관련 선로정수 측정","154kV 부천-원미#2T/L 선로정수 측정 (계통시험파트)","2020-10-13 14:00","2020-10-13 18:00","2020-10-13 14:00","2020-10-13 18:00","연속"]
[99,"인천","부평","서인천C/C 154kV CB 6433","서인천복합S/Y 170kV #4G.Tr(6433) GIS 보통점검 공사","서인천복합S/Y 170kV #4G.Tr(6433) GIS 보통점검 공사","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[100,"인천","직할","임학계양#2 T/L","154kV임학-계양#2T/L 정밀점검","154kV임학-계양#2T/L 정밀점검","2020-10-14 09:30","2020-10-16 18:00","2020-10-14 09:30","2020-10-16 18:00","연속"]
[101,"인천","직할","부개원미#1 T/L","원미S/S 부개원미#1T/L 170kV GIS 조작시험","원미S/S 부개원미#1T/L 170kV GIS 조작시험","2020-10-15 09:30","2020-10-15 14:00","2020-10-15 09:30","2020-10-15 14:00","연속"]
[102,"인천","직할","부개원미#2 T/L","원미S/S 부개원미#2T/L 170kV GIS 조작시험","원미S/S 부개원미#2T/L 170kV GIS 조작시험","2020-10-15 14:00","2020-10-15 18:00","2020-10-15 14:00","2020-10-15 18:00","연속"]
[103,"인천","직할","고강화곡#1 T/L","고강S/S 고강화곡#1T/L 170kV GIS 강화조작시험","고강S/S 고강화곡#1T/L 170kV GIS 강화조작시험","2020-10-17 09:30","2020-10-17 14:00","2020-10-17 09:30","2020-10-17 14:00","연속"]
[104,"인천","직할","고강화곡#2 T/L","고강S/S 고강화곡#2T/L 170kV GIS 강화조작시험","고강S/S 고강화곡#2T/L 170kV GIS 강화조작시험","2020-10-17 14:00","2020-10-17 18:00","2020-10-17 14:00","2020-10-17 18:00","연속"]
[105,"인천","부평","신가좌주안#1 T/L","병행지선 설치구간 선로정수 측정","병행지선 설치구간 선로정수 측정 공사구간 : 신주CH~M/H#3","2020-10-18 10:00","2020-10-18 14:00","2020-10-18 10:00","2020-10-18 14:00","연속"]
[106,"인천","부평","신가좌주안#2 T/L","병행지선 설치구간 선로정수 측정","병행지선 설치구간 선로정수 측정 공사구간 : 신주CH~M/H#3","2020-10-18 14:00","2020-10-18 18:00","2020-10-18 14:00","2020-10-18 18:00","연속"]
[107,"인천","부평","인천CC북인천#1 T/L","인천복합S/Y 인천CC북인천#1 T/L GIS 정밀점검 공사","인천복합S/Y 인천CC북인천#1 T/L GIS 정밀점검 공사","2020-10-19 09:00","2020-10-21 18:00","2020-10-19 09:00","2020-10-21 18:00","연속"]
[108,"인천","부평","서인천C/C 154kV CB 6100","서인천복합S/Y 170kV #1BUS-TIE GIS 조작시험 공사","서인천복합S/Y 170kV #1BUS-TIE GIS 조작시험 공사","2020-10-21 09:00","2020-10-21 14:00","2020-10-21 09:00","2020-10-21 14:00","연속"]
[109,"인천","부평","인천T/P 154kV #65 BUS","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","2020-10-21 13:00","2020-10-21 18:00","2020-10-21 13:00","2020-10-21 18:00","연속"]
[110,"인천","부평","인천T/P 154kV #66 BUS","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","2020-10-21 13:00","2020-10-21 18:00","2020-10-21 13:00","2020-10-21 18:00","연속"]
[111,"인천","부평","인천CC북인천#2 T/L","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#1T/L GIS 정밀점검 관련 무부하 가압용","2020-10-21 13:00","2020-10-21 18:00","2020-10-21 13:00","2020-10-21 18:00","연속"]
[112,"인천","부평","서인천C/C 154kV CB 6200","서인천복합S/Y 170kV #2BUS-TIE GIS 조작시험 공사","서인천복합S/Y 170kV #2BUS-TIE GIS 조작시험 공사","2020-10-21 14:00","2020-10-21 18:00","2020-10-21 14:00","2020-10-21 18:00","연속"]
[113,"인천","부평","서인천C/C 154kV SEC CB 60610","서인천복합S/Y 170kV 60-61 BUS SEC GIS 조작시험 공사","서인천복합S/Y 170kV 60-61 BUS SEC GIS 조작시험 공사","2020-10-22 09:00","2020-10-22 14:00","2020-10-22 09:00","2020-10-22 14:00","연속"]
[114,"인천","부평","인천CC북인천#2 T/L","인천복합S/Y 인천CC북인천#2 T/L GIS 정밀점검 공사","인천복합S/Y 인천CC북인천#2 T/L GIS 정밀점검 공사","2020-10-22 09:00","2020-10-24 18:00","2020-10-22 09:00","2020-10-24 18:00","연속"]
[115,"인천","부평","서인천C/C 154kV SEC CB 65660","서인천복합S/Y 170kV 65-66 BUS SEC GIS 조작시험 공사","서인천복합S/Y 170kV 65-66 BUS SEC GIS 조작시험 공사","2020-10-22 14:00","2020-10-22 18:00","2020-10-22 14:00","2020-10-22 18:00","연속"]
[116,"인천","직할","중동화곡#1 T/L","중동S/S 중동화곡#1T/L 170kV GIS 초기점검","중동S/S 중동화곡#1T/L 170kV GIS 초기점검","2020-10-24 09:30","2020-10-24 14:00","2020-10-24 09:30","2020-10-24 14:00","연속"]
[117,"인천","부평","인천T/P 154kV #65 BUS","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","2020-10-24 13:00","2020-10-24 18:00","2020-10-24 13:00","2020-10-24 18:00","연속"]
[118,"인천","부평","인천CC북인천#1 T/L","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","2020-10-24 13:00","2020-10-24 18:00","2020-10-24 13:00","2020-10-24 18:00","연속"]
[119,"인천","부평","인천T/P 154kV #66 BUS","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","인천복합S/Y 인천CC북인천#2T/L GIS 정밀점검 관련 무부하 가압용","2020-10-24 13:00","2020-10-24 18:00","2020-10-24 13:00","2020-10-24 18:00","연속"]
[120,"인천","직할","중동화곡#2 T/L","중동S/S 중동화곡#2T/L 170kV GIS 초기점검","중동S/S 중동화곡#2T/L 170kV GIS 초기점검","2020-10-24 14:00","2020-10-24 18:00","2020-10-24 14:00","2020-10-24 18:00","연속"]
[121,"인천","김포","왕길양촌#1 T/L","김포전력지사-양촌S/S 광케이블 시설공사","김포전력지사-양촌S/S 광케이블 시설(OPGW 1.49km, OFC 2.8km)","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[122,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사(#60BUS 무부하 및 BUS-TIE 대용) - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-26 18:00","2020-10-27 09:00","2020-10-26 18:00","2020-10-27 09:00","연속"]
[123,"인천","시흥","동시화서시화 T/L","서시화S/S 170kV GIS 대체공사","○ 서시화S/S 170kV GIS 대체공사(#65BUS 무부하 및 BUS-TIE 대용) - 북시화서시화#1T/L, #1M.Tr 1차, 170kV BUS-TIE 대체","2020-10-28 18:00","2020-10-29 18:00","2020-10-28 18:00","2020-10-29 18:00","연속"]
[124,"인천","부평","인천CC포스코CC#1 T/L","인천복합S/Y 인천CC포스코CC#1 T/L GIS 정밀점검 공사","인천복합S/Y 인천CC포스코CC#1 T/L GIS 정밀점검 공사","2020-10-29 09:00","2020-10-31 18:00","취소","취소","연속"]
[125,"인천","부평","인천CC북인천#1 T/L","인천복합S/Y 인천CC포스코CC#1T/L GIS 정밀점검 무부하 가압용","인천복합S/Y 인천CC포스코CC#1T/L GIS 정밀점검 무부하 가압용","2020-10-31 13:00","2020-10-31 18:00","취소","취소","연속"]
[126,"인천","부평","인천T/P 154kV #66 BUS","인천복합S/Y 인천CC포스코CC#1T/L GIS 정밀점검 무부하 가압용","인천복합S/Y 인천CC포스코CC#1T/L GIS 정밀점검 무부하 가압용","2020-10-31 13:00","2020-10-31 18:00","취소","취소","연속"]
[127,"인천","직할","고강S/S 154kV #1 BUS","154kV 고강-화곡(증) 지중T/L 건설공사","XLPE 2000/1200㎟ 1C-2.4km","2020-10-31 14:00","2020-10-31 15:00","2020-10-31 14:00","2020-10-31 15:00","연속"]
[128,"인천","직할","고강S/S 154kV #2 BUS","154kV 고강-화곡(증) 지중T/L 건설공사","XLPE 2000/1200㎟ 1C-2.4km","2020-10-31 15:00","2020-11-01 15:00","2020-10-31 15:00","2020-11-01 15:00","연속"]
[129,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(#1BUS 시험가압)","170kV GIS #1BUS 시험가압","2020-10-20 17:00","2020-10-22 10:00","2020-10-20 17:00","2020-10-22 10:00","연속"]
[130,"경기북부","고양","신덕은금촌#2 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#1T/L 170kV GIS 월붓싱 철거시 안전이격확보","2020-10-10 09:00","2020-10-10 17:00","2020-10-10 09:00","2020-10-10 17:00","연속"]
[131,"경기북부","고양","양주금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#1T/L 170kV GIS 월붓싱 설치시 안전이격확보","2020-10-24 09:00","2020-10-24 17:00","취소","취소","연속"]
[132,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(교체 GIS 시험가압)","교체 170kV GIS 시험가압","2020-10-31 17:00","2020-11-02 10:00","2020-10-31 17:00","2020-11-02 10:00","연속"]
[133,"경기북부","고양","신덕은금촌#2 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#1T/L 170kV GIS 월붓싱 설치시 안전이격확보","2020-10-24 09:00","2020-10-24 17:00","2020-10-24 09:00","2020-10-24 17:00","연속"]
[134,"경기북부","고양","신덕은금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사","금촌S/S 신덕은-금촌#1T/L GIS 교체공사","2020-10-05 09:00","2020-11-02 15:00","2020-10-05 09:00","2020-11-02 15:00","연속"]
[135,"경기북부","고양","월롱금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(#2BUS 시험가압)","170kV GIS #2BUS 시험가압","2020-10-08 17:00","2020-10-09 10:00","2020-10-08 17:00","2020-10-09 10:00","연속"]
[136,"경기북부","고양","양주금촌#1 T/L","2020년 금촌S/S 170kV GIS 교체공사(안전이격 확보)","신덕은-금촌#1T/L 170kV GIS 월붓싱 철거시 안전이격확보","2020-10-10 09:00","2020-10-10 17:00","취소","취소","연속"]
[137,"경기북부","고양","남면백석#2 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검","2020-10-14 08:00","2020-10-14 18:00","취소","취소","연속"]
[138,"경기북부","고양","남면백석#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검","2020-10-13 08:00","2020-10-13 18:00","취소","취소","연속"]
[139,"경기북부","고양","문산월롱#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검","2020-10-29 08:00","2020-10-29 18:00","2020-10-29 08:00","2020-10-29 18:00","연속"]
[140,"경기북부","고양","문산월롱#2 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검","2020-10-30 08:00","2020-10-30 18:00","2020-10-30 08:00","2020-10-30 18:00","연속"]
[141,"경기북부","고양","신덕은문산#2 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검(안전이격거리 확보휴전)","2020-10-30 08:00","2020-10-30 18:00","2020-10-30 08:00","2020-10-30 18:00","연속"]
[142,"경기북부","고양","신덕은문산#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전설비 초기점검(안전이격거리 확보휴전)","2020-10-29 08:00","2020-10-29 18:00","2020-10-29 08:00","2020-10-29 18:00","연속"]
[143,"경기북부","고양","일산호수#1 T/L","20~21년 고양전력지사 변전정비회사 총액공사","송전선로 보호배전반 교체공사","2020-10-20 09:00","2020-10-23 18:00","취소","취소","연속"]
[144,"경기북부","고양","양주고양#1 T/L","고양시국도대체우회도로 이설공사","철탑 : 3기설치, 2기철거 전력선 : 0.854 km교체","2020-10-26 07:00","2020-10-31 18:00","2020-10-26 07:00","2020-10-31 18:00","연속"]
[145,"경기북부","구리","가평청평HP#2 T/L","2020년 가공송전 순시점검 위탁공사","154kV 가평-청평HPT/L 정밀점검","2020-10-26 08:00","2020-10-30 18:00","2020-10-26 08:00","2020-10-30 18:00","연속"]
[146,"경기북부","구리","가평청평HP#1 T/L","2020년 가공송전 순시점검 위탁공사","154kV 가평-청평HPT/L 정밀점검","2020-10-19 08:00","2020-10-23 18:00","2020-10-19 08:00","2020-10-23 18:00","연속"]
[147,"경기북부","구리","구리신내#1 T/L","`20~21 구리전력 변전정비 총액공사","구리S/S 구리-신내#1T/L GIS 조작시험","2020-10-08 09:00","2020-10-08 18:00","2020-10-08 09:00","2020-10-08 18:00","연속"]
[148,"경기북부","구리","신장덕소#1 T/L","`20~21 구리전력 변전정비 총액공사","덕소S/S 신장-덕소#1T/L GIS 초기점검","2020-10-13 09:00","2020-10-13 14:00","2020-10-13 09:00","2020-10-13 14:00","연속"]
[149,"경기북부","구리","신장덕소#2 T/L","`20~21 구리전력 변전정비 총액공사","덕소S/S 신장-덕소#2T/L GIS 초기점검","2020-10-13 14:00","2020-10-13 18:00","2020-10-13 14:00","2020-10-13 18:00","연속"]
[150,"경기북부","구리","덕소팔당HP T/L","성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 덕소-팔당-청평hpT/L No.38(CH 병가)","2020-10-14 13:00","2020-10-14 18:00","2020-10-14 13:00","2020-10-14 18:00","연속"]
[151,"경기북부","구리","덕소진건#1 T/L","성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 덕소-진건#1T/L No.3,14","2020-10-26 07:00","2020-10-26 18:00","2020-10-26 07:00","2020-10-26 18:00","연속"]
[152,"경기북부","구리","덕소진건#2 T/L","성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 덕소-진건#2T/L No.2,14","2020-10-27 07:00","2020-10-27 18:00","2020-10-27 07:00","2020-10-27 18:00","연속"]
[153,"경기북부","구리","덕소팔당HP청평HP T/L","성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 덕소-팔당-청평hpT/L No.68(38호 CH 병가)","2020-10-14 07:00","2020-10-14 13:00","2020-10-14 07:00","2020-10-14 13:00","연속"]
[154,"경기북부","구리","미금화양 T/L","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체","2020-10-12 09:00","2020-10-16 18:00","취소","취소","연속"]
[155,"경기북부","구리","미금S/S 154kV CB 6200","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - #61-66 BUS TIe GIS 관련 감시제어계측 포인트이관 (→SA) - #61-66 BUS TIe GIS LCP 및 모자익반 제어케이블 철거 및 재결선","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[156,"경기북부","구리","미금S/S 154kV SEC CB 65660","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - #65-66 BUS SEC GIS 관련 감시제어계측 포인트이관 (→SA) - #65-66 BUS SEC GIS LCP 및 모자익반 제어케이블 철거 및 재결선","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[157,"경기북부","구리","미금S/S 154kV CB 6300","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - #62-67 BUS TIe GIS 관련 감시제어계측 포인트이관 (→SA) - #62-67 BUS TIe GIS LCP 및 모자익반 제어케이블 철거 및 재결선","2020-10-05 09:00","2020-10-09 18:00","2020-10-05 09:00","2020-10-09 18:00","연속"]
[158,"경기북부","구리","미금광장 T/L","154kV 미금-광장T/L 정밀점검","- No.3등 철탑21기 정밀점검","2020-10-05 09:00","2020-10-07 18:00","취소","취소","연속"]
[159,"경기북부","구리","미금S/S 154kV SEC CB 66670","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - #66-67 BUS SEC GIS 관련 감시제어계측 포인트이관 (→SA) - #66-67 BUS SEC GIS LCP 및 모자익반 제어케이블 철거 및 재결선","2020-10-05 09:00","2020-10-09 18:00","2020-10-05 09:00","2020-10-09 18:00","연속"]
[160,"경기북부","구리","서종청평PP#1 T/L","154kV 서종-청평PPT/L 전선접속개소 전선교체공사","154kV 서종-청평PP#1T/L No.58~60, 61~63 전선접속개소 전선교체공사","2020-10-05 07:00","2020-10-10 18:00","취소","취소","연속"]
[161,"경기북부","구리","서종S/S 154kV CB 6100","154kV 서종S/S #3M.Tr 증설공사","170kV GIS 1CCT 증설(#3M.Tr Main)","2020-10-05 09:00","2020-10-16 18:00","2020-10-05 09:00","2020-10-16 18:00","연속"]
[162,"경기북부","구리","서종S/S 154kV #2 BUS","154kV 서종S/S #3M.Tr 증설용 개폐장치 설치공사","170kV GIS 1CCT 증설","2020-10-05 09:00","2020-10-09 18:00","2020-10-05 09:00","2020-10-09 18:00","연속"]
[163,"경기북부","구리","서종S/S 154kV #60-#65 BUS TIE GIS","154kV 서종S/S #3M.Tr 설치공사","154kV M.Tr 1Bank 설치 - 무부하가압","2020-10-28 09:00","2020-10-30 18:00","취소","취소","연속"]
[164,"경기북부","구리","서종S/S 154kV #2 BUS","154kV 서종S/S #3M.Tr 설치공사","154kV M.Tr 1Bank 설치 - 무부하가압","2020-10-28 09:00","2020-10-30 18:00","2020-10-28 09:00","2020-10-30 18:00","연속"]
[165,"경기북부","구리","동서울서종#2 T/L","154kV 서종S/S #3M.Tr 설치공사","154kV M.Tr 1Bank 설치 - 무부하가압","2020-10-28 09:00","2020-10-30 18:00","2020-10-28 09:00","2020-10-30 18:00","연속"]
[166,"경기북부","구리","서종S/S 154kV #1 BUS","154kV 서종S/S #3M.Tr 증설용 개폐장치 설치공사","170kV GIS 1CCT 증설","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[167,"경기북부","구리","서종청평PP#2 T/L","154kV 서종-청평PPT/L 전선접속개소 전선교체공사","154kV 서종-청평PP#2T/L No.58~60, 61~63 전선접속개소 전선교체공사","2020-10-12 07:00","2020-10-17 18:00","취소","취소","연속"]
[168,"경기북부","구리","신포천포천#1 T/L","장기사용 성능저하 국산현수애자 교체공사 병가선로","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 신포천-포천#1T/L","2020-10-12 08:00","2020-10-12 18:00","2020-10-12 08:00","2020-10-12 18:00","연속"]
[169,"경기북부","구리","신포천전곡#1 T/L","장기사용 성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 신포천-전곡#1T/L","2020-10-13 13:00","2020-10-13 18:00","2020-10-13 13:00","2020-10-13 18:00","연속"]
[170,"경기북부","구리","운천전곡#1 T/L","장기사용 성능저하 국산현수애자 교체공사 병가선로","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 운천-전곡#1T/L","2020-10-13 08:00","2020-10-13 13:00","2020-10-13 08:00","2020-10-13 13:00","연속"]
[171,"경기북부","구리","운천전곡#2 T/L","장기사용 성능저하 국산현수애자 교체공사 병가선로","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 운천-전곡#2T/L","2020-10-13 13:00","2020-10-13 18:00","2020-10-13 13:00","2020-10-13 18:00","연속"]
[172,"경기북부","구리","청평HP의암HP T/L","154kV 청평HP-의암HPT/L 피뢰기 및 항공장애표시구 설치공사","154kV 청평HP-의암HPT/L 피뢰기(32~68호) 및 항공장애표시구 (42~42.1 등 12경간) 설치공사","2020-10-12 07:00","2020-10-16 18:00","취소","취소","연속"]
[173,"경기북부","구리","청평H/P 154kV CB 6133","`20~21 구리전력 변전정비 총액공사","청평H/P 154kV #1M.Tr 2차 GCB 보통점검","2020-10-26 09:00","2020-10-26 18:00","2020-10-26 09:00","2020-10-26 18:00","연속"]
[174,"경기북부","구리","청평H/P 154kV CB 6233","`20~21 구리전력 변전정비 총액공사","청평H/P 154kV #2M.Tr 2차 GCB 보통점검","2020-10-29 09:00","2020-10-29 18:00","2020-10-29 09:00","2020-10-29 18:00","연속"]
[175,"경기북부","구리","청평P/P 154kV CB 6133","`20~21 구리전력 변전정비 총액공사","청평P/P 154kV #1M.Tr 2차 GCB 조작시험, 전자변교체","2020-10-14 09:00","2020-10-14 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[176,"경기북부","구리","포천운천#2 T/L","장기사용 성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 포천-운천#2T/L","2020-10-13 08:00","2020-10-13 13:00","2020-10-13 08:00","2020-10-13 13:00","연속"]
[177,"경기북부","구리","포천운천#1 T/L","장기사용 성능저하 국산현수애자 교체공사","ㅇ 성능저하 애자교체공사 - 대상 : 154kV 포천-운천#1T/L","2020-10-12 08:00","2020-10-12 18:00","2020-10-12 08:00","2020-10-12 18:00","연속"]
[178,"경기북부","구리","포천S/S 154kV #1 BUS","포천S/S BUS-TIE 이설공사 (옥내화 부지확보)","○ 포천S/S 154kV Sh.C 철거 - 154kV #1Sh.C DS - #60BUS 간 인하선 철거","2020-10-06 08:00","2020-10-06 18:00","2020-10-06 08:00","2020-10-06 18:00","연속"]
[179,"경기북부","직할","금오상계#1 T/L","2020년 가공송전선로 순시점검 위탁공사","피뢰기 특별점검","2020-10-26 08:00","2020-10-28 18:00","2020-10-26 08:00","2020-10-28 18:00","연속"]
[180,"경기북부","직할","신의정부금오#2 T/L","20~21 직할 변전정비회사 총액공사","□ GIS 조작시험, 수분, SO2 측정(금오, 신의정부 양단)","2020-10-30 10:00","2020-10-30 18:00","2020-10-30 10:00","2020-10-30 18:00","연속"]
[181,"경기북부","직할","신의정부금오#1 T/L","20~21 직할 변전정비회사 총액공사","□ GIS 조작시험, 수분, SO2 측정(금오, 신의정부 양단)","2020-10-29 10:00","2020-10-29 18:00","취소","취소","연속"]
[182,"경기북부","직할","신포천동두천#1 T/L","2020년 가공송전선로 순시점검 위탁공사","154kV 옥정-동두천#1T/L 휴전 병가 (1루트 2회선)","2020-10-14 08:00","2020-10-15 18:00","2020-10-14 08:00","2020-10-15 18:00","연속"]
[183,"경기북부","직할","옥정동두천#1 T/L","2020년 가공송전선로 순시점검 위탁공사","전선접속개소 편심진단","2020-10-14 08:00","2020-10-15 18:00","2020-10-14 08:00","2020-10-15 18:00","연속"]
[184,"경기북부","직할","신의정부금오#1 T/L","신의정부S/S 효성제 GIS 발청보수공사","신의정부S/S 154kV 효성제 GIS 발청보수공사(제작사)","2020-10-21 09:00","2020-10-23 18:00","2020-10-21 09:00","2020-10-23 18:00","연속"]
[185,"경기북부","직할","신의정부S/S 154kV #66 BUS","신의정부S/S 효성제 GIS 발청보수공사","신의정부S/S 154kV 효성제 GIS 발청보수공사(제작사)","2020-10-21 09:00","2020-10-23 18:00","2020-10-21 09:00","2020-10-23 18:00","연속"]
[186,"경기북부","직할","신의정부S/S 154kV #65 BUS","신의정부S/S 효성제 GIS 발청보수공사","신의정부S/S 154kV 효성제 GIS 발청보수공사(제작사)","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[187,"경기북부","직할","신의정부S/S 154kV #60 BUS","신의정부S/S 효성제 GIS 발청보수공사","신의정부S/S 154kV 효성제 GIS 발청보수공사(제작사)","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[188,"경기북부","직할","신의정부S/S 154kV #61 BUS","신의정부S/S 효성제 GIS 발청보수공사","신의정부S/S 154kV 효성제 GIS 발청보수공사(제작사)","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[189,"경기북부","직할","신의정부송우#1 T/L","154kV 신의정부-송우T/L 지장송전선로 이설공사","- 154kV 신의정부-송우T/L No.37 교체(상향) - 154kV 신의정부-송우T/L No.38 철거 - 154kV 신의정부-송우T/L No.36-39 임시선로 구성 - 154kV 신의정부-송우T/L No.36-41 전선교체","2020-10-26 06:00","2020-11-23 18:00","2020-10-26 06:00","2020-11-23 18:00","연속"]
[190,"경기북부","직할","양주은평#1 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-은평#1 T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-10-26 08:00","2020-11-14 18:00","취소","취소","연속"]
[191,"경기북부","직할","양주S/S 154kV #62 BUS","양주S/S 154kV 옥외철구 변전설비 철거공사","○ #3M.Tr 휴전 후 STATCOM 부지설비 철거 - (구 옥외철구) 양주금촌 #1,2T/L, 양주고양 #2T/L CCT","2020-10-06 09:00","2020-10-07 18:00","2020-10-06 09:00","2020-10-07 18:00","매일"]
[192,"경기북부","직할","양주S/S 154kV #67 BUS","양주S/S 154kV 옥외철구 변전설비 철거공사","○ #3M.Tr 휴전 후 STATCOM 부지설비 철거 - (구 옥외철구) 양주금촌 #1,2T/L, 양주고양 #2T/L CCT","2020-10-06 09:00","2020-10-07 18:00","2020-10-06 09:00","2020-10-07 18:00","매일"]
[193,"경기북부","직할","양주S/S 154kV #60 BUS","양주S/S 154kV #62D.Tr 이설 및 60BUS 철구설비 철거","양주S/S 154kV #62D.Tr 이설 및 60BUS 철구설비 철거 - 60BUS 옥외철구 설비 철거(61BAY 제외)","2020-10-12 09:00","2020-10-30 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[194,"경기북부","직할","양주S/S 154kV #60 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-10-23 09:00","2020-10-24 18:00","2020-10-25 09:00","2020-10-26 18:00","연속"]
[195,"경기북부","직할","양주쌍문#1 T/L","20-21년 가공송전 정비회사 총액공사","ㅇ 성능저하 국산애자 교체공사","2020-10-26 07:00","2020-10-26 18:00","취소","취소","연속"]
[196,"경기북부","직할","양주고양#2 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-고양#2T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-10-05 08:00","2020-10-24 18:00","2020-10-07 08:00","2020-10-26 18:00","연속"]
[197,"경기북부","직할","양주금촌#1 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-금촌#1T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-10-05 08:00","2020-10-24 18:00","2020-10-07 08:00","2020-10-26 18:00","연속"]
[198,"경기북부","직할","양주S/S 154kV #65 BUS","양주S/S 154kV #62D.Tr 이설 및 65BUS 철구설비 철거","양주S/S 154kV #62D.Tr 이설 및 65BUS 철구설비 철거 - 65BUS 옥외철구 설비 철거(61BAY 제외)","2020-10-05 09:00","2020-10-30 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[199,"경기북부","직할","양주지축#1 T/L","양주S/S 154kV 인출T/L 지중화공사","154kV 양주-지축#1 T/L 구내 지중화 ○ 구간 : 신설 EBA~신설 EBG ○ 내용 : 케이블 포설 및 접속","2020-10-26 08:00","2020-11-14 18:00","취소","취소","연속"]
[200,"경기북부","직할","양주쌍문#2 T/L","20-21년 가공송전 정비회사 총액공사","ㅇ 성능저하 국산애자 교체공사","2020-10-27 07:00","2020-10-27 18:00","취소","취소","연속"]
[201,"경기북부","직할","양주S/S 154kV #61 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-10-23 09:00","2020-10-24 18:00","2020-10-25 09:00","2020-10-26 18:00","연속"]
[202,"경기북부","직할","양주S/S 154kV #67 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-10-24 00:00","2020-10-24 18:00","2020-10-26 00:00","2020-10-26 18:00","연속"]
[203,"경기북부","직할","양주S/S 154kV #62 BUS","양주S/S 154kV 인출T/L 지중화공사","상시험 및 무부하가압용","2020-10-23 09:00","2020-10-23 23:59","2020-10-25 09:00","2020-10-25 23:59","연속"]
[204,"경기북부","직할","옥정송우#1 T/L","20~21 직할 변전정비회사 총액공사","□ GIS 조작시험 및 수분, SO2 측정","2020-10-27 10:00","2020-10-27 14:00","2020-10-27 10:00","2020-10-27 14:00","연속"]
[205,"경기북부","직할","옥정양주열병합#2 T/L","20~21 직할 변전정비회사 총액공사","□ GIS 조작시험 및 수분, SO2 측정","2020-10-23 14:00","2020-10-23 18:00","2020-10-23 14:00","2020-10-23 18:00","연속"]
[206,"경기북부","직할","옥정양주열병합#1 T/L","20~21 직할 변전정비회사 총액공사","□ GIS 조작시험 및 수분, SO2 측정","2020-10-23 10:00","2020-10-23 14:00","2020-10-23 10:00","2020-10-23 14:00","연속"]
[207,"경기북부","직할","용현도봉#2 T/L","2020년 가공송전선로 순시점검 위탁공사","피뢰기 특별점검","2020-10-26 08:00","2020-10-28 18:00","2020-10-26 08:00","2020-10-28 18:00","연속"]
[208,"경기","군포","화성마도 T/L","154kV 화성-마도T/L 초기점검(20년 가공송전 위탁공사)","154kV 화성-마도T/L No.51부하측~52호(C/H)","2020-10-24 09:00","2020-10-24 18:00","2020-10-24 09:00","2020-10-24 18:00","연속"]
[209,"경기","군포","장덕마도 T/L","154kV 장덕-마도T/L 초기점검(20년 가공송전 위탁공사)","154kV 장덕-마도T/L No.51부하측~52호(C/H)","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[210,"경기","군포","마도사강#2 T/L","154kV 마도-사강#2T/L 초기점검(20년 가공송전 위탁공사)","154kV 마도-사강#2T/L No.52호(C/H)~53호(전원측)","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[211,"경기","군포","마도사강#1 T/L","154kV 마도-사강#1T/L 초기점검(20년 가공송전 위탁공사)","154kV 마도-사강#1T/L No.52호(C/H)~53호(전원측)","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[212,"경기","군포","목내안산복합#1 T/L","목내S/S 목내-안산C/C #1T/L GIS 정밀점검","목내S/S 목내-안산C/C #1T/L GIS 정밀점검, 안산C/C측 보통점검(병행)","2020-10-12 09:00","2020-10-13 18:00","2020-10-12 09:00","2020-10-13 18:00","연속"]
[213,"경기","군포","목내안산복합#2 T/L","목내S/S 목내-안산C/C #2T/L GIS 정밀점검","목내S/S 목내-안산C/C #2T/L GIS 정밀점검, 안산C/C측 보통점검(병행)","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[214,"경기","군포","반월시화#2 T/L","반월-시화#2T/L 보호반 대체공사","반월-시화#2T/L 보호반 대체공사 반월S/S GIS 하자점검 및 패킹보수, 시화S/S GIS 보통점검","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[215,"경기","군포","서안양소래 T/L","서안양-소래 일진제 DS key 불량 관련 현장 확인 및 조치 작업","서안양S/S 서안양-소래 일진제 DS key 불량 관련 현장 확인 및 조치 작업","2020-10-23 10:00","2020-10-23 14:00","2020-10-23 10:00","2020-10-23 14:00","연속"]
[216,"경기","군포","서안양S/S 154kV 삼천리#1T/L CB","삼천리#1 일진제 DS Key 불량 관련 현장 확인 및 조치","서안양S/S 삼천리#1 일진제 DS Key 불량 관련 현장 확인 및 조치","2020-10-23 14:00","2020-10-23 18:00","취소","취소","연속"]
[217,"경기","군포","서안양S/S 154kV 삼천리#2T/L CB","삼천리#2 일진제 DS Key 불량 관련 현장 확인 및 조치","서안양S/S 삼천리#2 일진제 DS Key 불량 관련 현장 확인 및 조치","2020-10-29 14:00","2020-10-29 18:00","취소","취소","연속"]
[218,"경기","군포","서서울#2서안양 T/L","서서울2-서안양 일진제 DS key 불량 관련 현장 확인 및 조치 작업","서안양S/S 서서울2-서안양 일진제 DS key 불량 관련 현장 확인 및 조치 작업","2020-10-22 10:00","2020-10-22 18:00","2020-10-22 10:00","2020-10-22 18:00","연속"]
[219,"경기","군포","성곡중시화 T/L","성곡-중시화T/L 보호반 대체공사","성곡-중시화T/L 보호반 대체공사","2020-10-14 08:00","2020-10-16 18:00","취소","취소","연속"]
[220,"경기","군포","시화중시화 T/L","시화-중시화T/L 보호반 대체공사","시화-중시화T/L 보호반 대체공사 시화SS GIS 조작, 중시화SS GIS 보통점검","2020-10-19 08:00","2020-10-21 18:00","2020-10-19 14:00","2020-10-22 18:00","연속"]
[221,"경기","군포","시화성곡 T/L","시화S/S 시화-성곡T/L GIS 전자변히터설치","시화S/S 시화-성곡T/L GIS 전자변히터설치","2020-10-23 08:00","2020-10-23 18:00","2020-10-23 08:00","2020-10-23 18:00","연속"]
[222,"경기","군포","신안산성포#2 T/L","신안산-성포#2T/L 보호반 대체공사","신안산-성포#2T/L 보호반 대체공사","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[223,"경기","군포","신안산성포#1 T/L","신안산-성포#1T/L 보호반 대체공사","신안산-성포#1T/L 보호반 대체공사","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","연속"]
[224,"경기","군포","안산안산복합#1 T/L","안산복합,안산S/S 안산-안산복합#1T/L GIS 보통점검","안산복합,안산S/S 안산-안산복합#1T/L GIS 보통점검","2020-10-05 09:00","2020-10-05 14:00","2020-10-05 09:00","2020-10-05 14:00","연속"]
[225,"경기","군포","안산안산복합#2 T/L","안산복합,안산S/S 안산-안산복합#2T/L GIS 보통점검","안산복합,안산S/S 안산-안산복합#2T/L GIS 보통점검","2020-10-05 14:00","2020-10-05 18:00","2020-10-05 14:00","2020-10-05 18:00","연속"]
[226,"경기","군포","안산안산복합#3 T/L","안산복합,안산S/S 안산-안산복합#3T/L GIS 보통점검","안산복합,안산S/S 안산-안산복합#3T/L GIS 보통점검","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[227,"경기","동부","왕암가남#2 T/L","154kV왕암-가남T/L 국산애자 및 불량애자 교체공사","국산애자 및 불량애자 교체공사","2020-10-15 09:00","2020-10-17 18:00","2020-10-15 09:00","2020-10-17 18:00","매일"]
[228,"경기","동부","왕암가남#1 T/L","154kV왕암-가남T/L 국산애자 및 불량애자 교체공사","국산애자 및 불량애자 교체공사","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","매일"]
[229,"경기","동부","곤지암율현#1 T/L","154kV 오천-율현T/L 송전선로 정밀점검(안전이격거리 확보)","154kV 오천-율현#2T/L 송전선로 정밀점검 안전이격거리 확보","2020-10-31 09:00","2020-10-31 18:00","취소","취소","연속"]
[230,"경기","동부","곤지암율현#2 T/L","154kV 오천-율현T/L 송전선로 정밀점검(안전이격거리 확보)","154kV 오천-율현#1T/L 송전선로 정밀점검 안전이격거리 확보","2020-10-25 09:00","2020-10-25 18:00","2020-10-25 09:00","2020-10-25 18:00","연속"]
[231,"경기","동부","분당S/S 154kV CB 6100","20년 동부 변전정비회사 총액공사","분당:6100 GIS(보통),6200 GIS(조작)43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-10-15 09:30","2020-10-15 18:00","2020-10-15 09:30","2020-10-15 18:00","연속"]
[232,"경기","동부","성현분당#1 T/L","20년 동부 변전정비회사 총액공사","성현:성현-분당#1T/L(조작),GIS전자변교체(H),43L/R 회로보완 확인 및 Remote 회로분리 시행, LA(초기) 성현-분당#2T/L(조작),GIS전자변교체(H),43L/R 회로보완 확인 및 Remote 회로분리 시행- GIS PNL 하부 습도계 불량]☞가능하다면 교체요망합니다.","2020-10-23 09:30","2020-10-23 14:00","2020-10-23 09:30","2020-10-23 14:00","연속"]
[233,"경기","동부","성현분당#2 T/L","20년 동부 변전정비회사 총액공사","성현:성현-분당#1T/L(조작),GIS전자변교체(H),43L/R 회로보완 확인 및 Remote 회로분리 시행, LA(초기) 성현-분당#2T/L(조작),GIS전자변교체(H),43L/R 회로보완 확인 및 Remote 회로분리 시행- GIS PNL 하부 습도계 불량]☞가능하다면 교체요망합니다.","2020-10-23 14:00","2020-10-23 18:00","2020-10-23 14:00","2020-10-23 18:00","연속"]
[234,"경기","동부","초월성현#1 T/L","20년 동부 변전정비회사 총액공사","성현:초월-성현#1T/L GIS(보통),GIS전자변교체(C),43L/R 회로보완 확인 및 Remote 회로분리 시행,LA(초기) 초월:초월-성현#1T/L GIS(조작),전자변 실리콘히터 설치, 43L/R 회로보완 확인 및 Remote 회로분리 시행,LA(초기)","2020-10-28 09:30","2020-10-28 18:00","2020-10-28 09:30","2020-10-28 18:00","연속"]
[235,"경기","동부","초월성현#2 T/L","20년 동부 변전정비회사 총액공사","성현:초월-성현#2T/L GIS(보통),GIS전자변교체(C),43L/R 회로보완 확인 및 Remote 회로분리 시행,LA(초기) 초월:초월-성현#2T/L GIS(조작),전자변 실리콘히터 설치, 43L/R 회로보완 확인 및 Remote 회로분리 시행,LA(초기)","2020-10-29 09:30","2020-10-29 18:00","2020-10-29 09:30","2020-10-29 18:00","연속"]
[236,"경기","동부","오천율현#1 T/L","154kV 오천-율현T/L 송전선로 정밀점검","154kV 오천-율현#1T/L 1~25호 송전선로 정밀점검(25기)","2020-10-25 09:00","2020-10-26 18:00","2020-10-25 09:00","2020-10-26 18:00","연속"]
[237,"경기","동부","오천율현#2 T/L","154kV 오천-율현T/L 송전선로 정밀점검","154kV 오천-율현#2T/L 1~25호 송전선로 정밀점검(25기)","2020-10-30 09:00","2020-10-31 18:00","취소","취소","연속"]
[238,"경기","동부","오천용인#2 T/L","154kV 용인-오천T/L 송전선로 정밀점검","154kV 용인-오천#2T/L 1~58호 송전선로 정밀점검(25기)","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[239,"경기","동부","오천용인#1 T/L","154kV 용인-오천T/L 송전선로 정밀점검","154kV 용인-오천#1T/L 1~58호 송전선로 정밀점검(25기)","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[240,"경기","동부","곤지암이천#2 T/L","20년 동부전력 170kV GIS 정밀점검공사","이천:곤지암-이천#2T/L 170kV GIS 정밀점검(~11)","2020-10-09 09:30","2020-10-11 18:00","2020-10-09 09:30","2020-10-11 18:00","연속"]
[241,"경기","동부","초월성현#1 T/L","20년 동부전력 170kV GIS 정밀점검공사","초월:#1M.Tr 170kV GIS 정밀점검(무부하가압)","2020-10-13 09:30","2020-10-14 18:00","2020-10-16 09:00","2020-10-17 18:00","매일"]
[242,"경기","성남","마북이의#3 T/L","마북S/S #3M.Tr 증설공사","마북S/S #3M.Tr 증설공사","2020-10-12 10:00","2020-10-23 17:00","2020-10-12 10:00","2020-10-23 17:00","연속"]
[243,"경기","성남","신용인S/S 154kV CB 6200","20년 성남전력 변전정비회사 총액공사","전자변교체","2020-10-23 09:00","2020-10-23 14:00","2020-10-23 09:00","2020-10-23 14:00","연속"]
[244,"경기","성남","신용인S/S 154kV #1 EM.Tr CB","20년 성남전력 변전정비회사 총액공사","세니온 IED 성능개선","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[245,"경기","직할","동안양안양CC#1 T/L","20년 직할 변전정비회사 총액공사","동안양S/S 안열 #1T/L GIS 보통점검","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[246,"경기","직할","동안양안양CC#2 T/L","20년 직할 변전정비회사 총액공사","동안양S/S 안열 #2T/L GIS 보통점검","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[247,"경기","직할","과천동안양#2 T/L","19-20년 지중송전 위탁정비공사","과천-동안양T/L 케이블헤드 및 피뢰기 점검","2020-10-20 09:00","2020-10-21 18:00","2020-10-20 09:00","2020-10-21 18:00","연속"]
[248,"경기","직할","의왕동안양#1 T/L","OPGW 항공장애표시구 설치공사","의왕-동안양T/L 39~40호 항공장애표시구 설치 공사","2020-10-05 09:00","2020-10-05 18:00","2020-10-05 09:00","2020-10-05 18:00","연속"]
[249,"경기","직할","남수원발안#2 T/L","154kV 발안-향남#2T/L 송전선로 정밀점검","154kV 발안-향남#2T/L(No.1~20) 송전선로 정밀점검 [안전이격거리 확보]","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","매일"]
[250,"경기","직할","발안향남#2 T/L","154kV 발안-향남#2T/L 송전선로 정밀점검","154kV 발안-향남#2T/L(No.1~20) 송전선로 정밀점검","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","매일"]
[251,"경기","직할","남수원발안#1 T/L","154kV 발안-향남#1T/L 송전선로 정밀점검","154kV 발안-향남#1T/L(No.1~20) 송전선로 정밀점검 [안전이격거리 확보]","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","매일"]
[252,"경기","직할","발안향남#1 T/L","154kV 발안-향남#1T/L 송전선로 정밀점검","154kV 발안-향남#1T/L(No.1~20) 송전선로 정밀점검","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","매일"]
[253,"경기","직할","남수원발안#2 T/L","발안S/S #5M.Tr 증설","GIS * 1CCT설치, 모선PT 이설","2020-10-30 09:00","2020-10-31 18:00","2020-10-30 09:00","2020-10-31 18:00","연속"]
[254,"경기","직할","남수원발안#2 T/L","발안S/S #5M.Tr 증설","GIS * 1CCT설치, 모선PT 이설","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","연속"]
[255,"경기","직할","남수원발안#1 T/L","발안S/S #5M.Tr 증설","GIS * 1CCT설치, 모선PT 이설","2020-10-13 09:00","2020-11-11 18:00","2020-10-13 09:00","2020-11-11 18:00","연속"]
[256,"경기","직할","서서울율전#2 T/L","20년 직할 변전정비회사 총액공사","율전S/S 서서울-율전#2T/L GIS 전자변 교체 유)전자변 보온커버(히터)설치","2020-10-19 09:00","2020-10-19 18:00","2020-10-19 09:00","2020-10-19 18:00","연속"]
[257,"경기","직할","서서울율전#1 T/L","20년 직할 변전정비회사 총액공사","율전S/S 서서울-율전#1T/L GIS 전자변 교체 유)전자변 보온커버(히터)설치","2020-10-15 09:00","2020-10-15 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[258,"경기","직할","화성남양#1 T/L","20년 직할 변전정비회사 총액공사","화성S/S 화성-남양#1,2T/L GIS 전자변 교체","2020-10-17 09:00","2020-10-17 14:00","2020-10-17 09:00","2020-10-17 14:00","연속"]
[259,"경기","직할","화성S/S 154kV CB 6300","20년 직할 변전정비회사 총액공사","화성S/S 6300 조작","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[260,"경기","직할","화성장덕 T/L","20년 직할 변전정비회사 총액공사","화성S/S 화성-장덕T/L 보호반 대체(~11)","2020-10-09 09:00","2020-10-11 18:00","2020-10-09 09:00","2020-10-11 18:00","연속"]
[261,"경기","직할","화성남양#2 T/L","20년 직할 변전정비회사 총액공사","화성S/S 화성-남양#1,2T/L GIS 전자변 교체","2020-10-17 14:00","2020-10-17 18:00","2020-10-17 14:00","2020-10-17 18:00","연속"]
[262,"경기","평택","서안성안성#2 T/L","20년 직할 송전정비회사 총액공사","서안성남사 #1 송전선로용 피뢰기설치 안전이격거리 확보","2020-10-05 08:00","2020-10-05 18:00","2020-10-05 08:00","2020-10-05 18:00","연속"]
[263,"경기","평택","서안성남사#1 T/L","20년 직할 송전정비회사 총액공사","송전선로용 피뢰기설치 1 20호","2020-10-05 08:00","2020-10-08 18:00","2020-10-05 08:00","2020-10-08 18:00","매일"]
[264,"경기","평택","서안성S/S 154kV #1 EM.Tr CB","서안성S/S 154kV #1 EM.Tr A 변압기 보통점검","서안성S/S 154kV #1 EM.Tr A 변압기 보통점검 / 보호반 성능 개선 / 1차,2차 GIS 보통점검","2020-10-14 10:00","2020-10-16 18:00","2020-10-14 10:00","2020-10-16 18:00","연속"]
[265,"경기","평택","서안성안성#1 T/L","20년 직할 송전정비회사 총액공사","송전선로용 피뢰기설치 30 34호","2020-10-09 08:00","2020-10-10 18:00","2020-10-09 08:00","2020-10-10 18:00","매일"]
[266,"경기","평택","서안성남사#2 T/L","20년 직할 송전정비회사 총액공사","송전선로용 피뢰기설치 1 5호","2020-10-09 08:00","2020-10-09 18:00","2020-10-09 08:00","2020-10-09 18:00","연속"]
[267,"경기","평택","서운안성#1 T/L","서운S/S 154kV 서운-안성#1T/L GIS 보통점검","서운S/S 154kV 서운-안성#1T/L GIS 보통점검","2020-10-31 10:00","2020-10-31 18:00","2020-10-31 10:00","2020-10-31 18:00","연속"]
[268,"경기","평택","평택오성CC#1 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-28 07:00","2020-10-29 18:00","2020-10-28 07:00","2020-10-29 18:00","연속"]
[269,"경기","평택","평택오성CC#2 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-12 07:00","2020-10-21 18:00","2020-10-12 07:00","2020-10-21 18:00","연속"]
[270,"경기","평택","송탄오성CC#2 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-16 07:00","2020-10-21 18:00","2020-10-16 07:00","2020-10-21 18:00","연속"]
[271,"경기","평택","평택오성CC#2 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-24 07:00","2020-10-29 18:00","2020-10-24 07:00","2020-10-29 18:00","연속"]
[272,"경기","평택","송탄오성CC#1 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-24 07:00","2020-10-29 18:00","2020-10-24 07:00","2020-10-29 18:00","연속"]
[273,"경기","평택","평택오성CC#1 T/L","평택S/S~오성CC간 지중화공사","[요청자 시행]154kV 평택-오성CCT/L No.3, 7 및 송탄-오성CCT/L No.1, 1.6 철탑개조(케이블헤드 설치), 가공선로 및 OPGW 철거,설치","2020-10-12 07:00","2020-10-21 18:00","2020-10-12 07:00","2020-10-21 18:00","연속"]
[274,"경기","평택","만호청북#1 T/L","345kV 신온양서서울외 2개T/L 지장이설","지장이설 본선로 구성 No.43, 44, 43-46 전력선교체","2020-10-30 07:00","2020-11-04 18:00","2020-10-30 07:00","2020-11-04 18:00","연속"]
[275,"경기","평택","청북평택#2 T/L","평택S/S 154kV 청북-평택#2 T/L 622DS 조작함 교체","평택S/S 154kV 청북-평택#2 T/L 622DS 조작함 교체","2020-10-06 10:00","2020-10-06 18:00","2020-10-06 10:00","2020-10-06 18:00","연속"]
[276,"경기","평택","평택S/S 154kV #2 BUS","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","2020-10-05 14:00","2020-10-05 18:00","2020-10-05 14:00","2020-10-05 18:00","연속"]
[277,"경기","평택","청북평택#1 T/L","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","2020-10-05 10:00","2020-10-05 18:00","2020-10-05 10:00","2020-10-05 18:00","연속"]
[278,"경기","평택","평택S/S 154kV #1 BUS","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","평택S/S 154kV 청북-평택#1 T/L DS 과열보수","2020-10-05 10:00","2020-10-05 14:00","2020-10-05 10:00","2020-10-05 14:00","연속"]
[279,"강원","강릉","강릉횡계#2 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-14 10:00","2020-10-14 18:00","2020-10-14 10:00","2020-10-14 18:00","연속"]
[280,"강원","강릉","강릉횡계#1 T/L","2020년 170kV GIS 하자점검","○ 2020년 170kV GIS 하자점검 : 강릉S/S 강릉-횡계#1T/L ○ 2020년 장기미동작 차단기 조작시험 : 횡계S/S 강릉횡계#1T/L","2020-10-19 10:00","2020-10-19 18:00","2020-10-19 10:00","2020-10-19 18:00","연속"]
[281,"강원","강릉","강릉횡계#1 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 불량애자교체 : 154kV 강릉횡계#1T/L No.33","2020-10-26 08:00","2020-10-26 18:00","2020-10-26 08:00","2020-10-26 18:00","연속"]
[282,"강원","강릉","동해강릉 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 154kV 강릉-횡계#1T/L 불량애자교체작업 4회선구간 휴전","2020-10-26 08:00","2020-10-26 18:00","2020-10-26 08:00","2020-10-26 18:00","연속"]
[283,"강원","강릉","신양양양양#1 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-12 10:00","2020-10-12 18:00","2020-10-12 10:00","2020-10-12 18:00","연속"]
[284,"강원","강릉","북평영동TP#2 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ SB댐퍼, 노후금구류, 스페이서 교체공사 : 154kV 강릉T/L No.1~8(작업자 안전을 위한 인접선로 휴전)","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[285,"강원","강릉","동해영동TP T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○SB댐퍼, 스페이서, 노후금구류 교체 : 154kV 동해분기T/L No.1~53(34기), 154kV 강릉T/L No.1~8(8기)","2020-10-05 08:00","2020-10-15 18:00","2020-10-05 08:00","2020-10-15 18:00","매일"]
[286,"강원","강릉","신제천주진#1 T/L","2020~2021년도 원주전력지사 송전정비회사 총액공사","○ 전선 접속개소 해소공사","2020-10-26 07:00","2020-10-29 18:00","2020-10-26 07:00","2020-10-29 18:00","연속"]
[287,"강원","강릉","신제천주진#2 T/L","2020~2021년도 원주전력지사 송전정비회사 총액공사","○ 전선 접속개소 해소공사","2020-10-30 07:00","2020-11-02 18:00","2020-10-30 07:00","2020-11-02 18:00","연속"]
[288,"강원","강릉","주진평창#2 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ SB댐퍼 교체 및 신설 : 154kV 주진평창 #2T/L No.2~ST(23기)","2020-10-27 08:00","2020-10-30 18:00","2020-10-27 08:00","2020-10-30 18:00","매일"]
[289,"강원","강릉","주진평창#1 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ SB댐퍼, 불량애자교체 : 154kV 주진평창T/L No.2~ST(23기)","2020-10-21 08:00","2020-10-26 18:00","2020-10-21 08:00","2020-10-26 18:00","매일"]
[290,"강원","강릉","횡계올림픽 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-16 10:00","2020-10-16 18:00","2020-10-16 10:00","2020-10-16 18:00","연속"]
[291,"강원","강릉","횡계평창 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-15 10:00","2020-10-15 18:00","2020-10-15 10:00","2020-10-15 18:00","연속"]
[292,"강원","동해","동해동영월 T/L","154kV 영월화력T/L No.124 안전이격확보공사","안전이격확보공사","2020-10-19 08:00","2020-10-23 18:00","2020-10-19 08:00","2020-10-23 18:00","연속"]
[293,"강원","동해","동해동영월 T/L","2020년 동해전력지사 장기미동작 차단기 조작시험","동해동영월T/L 장기미동작 차단기 조작시험","2020-10-21 09:00","2020-10-21 18:00","2020-10-21 09:00","2020-10-21 18:00","연속"]
[294,"강원","동해","동해T/P 154kV #2 BUS","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-10-13 09:00","2020-10-20 18:00","2020-10-13 09:00","2020-10-20 18:00","연속"]
[295,"강원","동해","삼척동해TP T/L","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-09-24 09:00","2020-10-23 18:00","2020-09-24 09:00","2020-10-23 18:00","연속"]
[296,"강원","동해","동해T/P 154kV #1 BUS","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-10-05 09:00","2020-10-12 18:00","2020-10-05 09:00","2020-10-12 18:00","연속"]
[297,"강원","동해","태백삼척GP#2 T/L","2020년 동해전력지사 장기미동작 차단기 조작시험","태백-삼척GP#2 T/L 장기미동작 차단기 조작시험","2020-10-22 09:00","2020-10-22 18:00","취소","취소","연속"]
[298,"강원","동해","삼척GP 154kV SEC CB 61620","삼척GP 170kV GIS 스페이서 교체공사","1. 가스 누기부 스페이서 교체","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[299,"강원","동해","정선영월CC T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48)31.688kM 교체 - 항공장애표시구 71개 철거 및 설치","2020-10-21 08:00","2020-11-14 18:00","2020-10-21 08:00","2020-11-14 18:00","연속"]
[300,"강원","원주","남원주원주#1 T/L","2020년 원주전력지사 변전정비회사 총액공사","임시 SPS 계전기 및 제어케이블 철거","2020-10-21 09:00","2020-10-21 18:00","2020-10-21 09:00","2020-10-21 18:00","연속"]
[301,"강원","원주","원주서원주#1 T/L","세니온제 보호배전반 성능개선","- 보호계전기 성능개선 시행","2020-10-14 10:30","2020-10-14 18:00","2020-10-14 10:30","2020-10-14 18:00","연속"]
[302,"강원","원주","홍천상남#2 T/L","2020년 원주전력지사 변전정비회사 총액공사","상시여자형 보조Ry 과열 및 이음발생 교체 - K102, VX 게전기","2020-10-22 09:00","2020-10-22 18:00","2020-10-22 09:00","2020-10-22 18:00","연속"]
[303,"강원","원주","횡성홍천#1 T/L","154kV 홍천T/L No.60~67 안전이격 확보공사","○ 철탑교체 : 4기(No.60,61,62,63)","2020-10-12 07:00","2020-10-21 18:00","2020-10-12 07:00","2020-10-21 18:00","연속"]
[304,"강원","원주","홍천소양강HP T/L","2020~2021년 강원직할 송전정비회사 총액공사","안전이격확보공사(철탑교체 및 전력선 교체)","2020-10-20 07:00","2020-10-23 18:00","2020-10-20 07:00","2020-10-23 18:00","연속"]
[305,"강원","원주","횡성홍천#1 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV GIS 월부싱교체 안전이격확보","2020-10-07 08:00","2020-10-07 18:00","2020-10-07 08:00","2020-10-07 18:00","연속"]
[306,"강원","원주","횡성홍천#2 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV 장기사용 GIS 철거/설치 ㅇ 디지털화공사 케이블 철거 및 광케이블 포설 ㅇ SA 운영장치 시험","2020-10-05 10:00","2020-10-30 18:00","2020-10-05 10:00","2020-10-30 18:00","연속"]
[307,"강원","원주","횡성홍천#1 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV GIS 월부싱교체 안전이격확보","2020-10-16 08:00","2020-10-17 18:00","취소","취소","매일"]
[308,"강원","직할","남춘천춘천열병합#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량애자 교체","2020-10-08 09:00","2020-10-08 18:00","2020-10-08 09:00","2020-10-08 18:00","연속"]
[309,"강원","직할","남춘천춘천열병합#1 T/L","2020년 하반기 강원 직할 154kV GIS 정밀점검","154kV GIS 정밀점검","2020-10-29 09:00","2020-10-31 18:00","2020-10-29 09:00","2020-10-31 18:00","연속"]
[310,"강원","직할","홍천남춘천 T/L","2020년 하반기 장기 미동작 차단기 조작시험","남춘천S/S 154kV 홍천-남춘천 T/L 차단기 조작시험","2020-10-19 10:00","2020-10-19 14:00","취소","취소","연속"]
[311,"강원","직할","남춘천춘천 T/L","2020~2021년 강원직할 송전정비회사 총액공사","안전이격확보공사(철탑교체 및 전력선 교체)","2020-10-16 07:00","2020-10-19 18:00","취소","취소","연속"]
[312,"강원","직할","남춘천춘천 T/L","2020년 하반기 강원 직할 154kV GIS 정밀점검","154kV GIS 정밀점검","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[313,"강원","직할","북춘천화천HP T/L","2020년 하반기 장기 미동작 차단기 조작시험","북춘천S/S 154kV 북춘천-화천HP T/L 차단기 조작시험","2020-10-14 14:00","2020-10-14 18:00","2020-10-14 14:00","2020-10-14 18:00","연속"]
[314,"강원","직할","서홍천춘천열병합 T/L","2020년 하반기 장기 미동작 차단기 조작시험","서홍천S/S 154kV 서홍천-춘천열병합 T/L 차단기 조작시험","2020-10-15 10:00","2020-10-15 18:00","2020-10-15 10:00","2020-10-15 18:00","연속"]
[315,"강원","직할","양구화천HP#1 T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량개소 정비(B-C링크 철거)","2020-10-12 08:00","2020-10-12 13:00","2020-10-12 08:00","2020-10-12 13:00","연속"]
[316,"강원","직할","상남인제#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","섬락애자 교체 No.91 등 4기","2020-10-06 07:00","2020-10-06 18:00","2020-10-06 07:00","2020-10-06 18:00","연속"]
[317,"강원","직할","춘천소양강HP T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량애자교체","2020-10-15 07:00","2020-10-15 18:00","2020-10-15 07:00","2020-10-15 18:00","연속"]
[318,"강원","직할","춘천북춘천#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","와이어형 추락방지시설설치 및 B-C링크 철거","2020-10-14 07:00","2020-10-14 18:00","2020-10-14 07:00","2020-10-14 18:00","연속"]
[319,"강원","직할","춘천북춘천#1 T/L","2020~2021년 강원직할 송전정비회사 총액공사","와이어형 추락방지시설설치 및 B-C링크 철거","2020-10-13 07:00","2020-10-13 18:00","2020-10-13 07:00","2020-10-13 18:00","연속"]
[320,"강원","직할","춘천H/P 154kV CB 6233","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[321,"강원","직할","춘천H/P 154kV CB 6133","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[322,"강원","직할","춘천H/P 154kV #60 BUS","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[323,"강원","직할","청평PP춘천열병합 T/L","2020년 하반기 장기 미동작 차단기 조작시험","춘천열병합S/Y 154kV 청평PP-춘천열병합T/L 차단기 조작시험","2020-10-07 14:00","2020-10-07 18:00","2020-10-07 14:00","2020-10-07 18:00","연속"]
[324,"강원","직할","춘천열병합 154kV CB 6283","2020년 하반기 장기 미동작 차단기 조작시험","춘천열병합S/Y Stataion Aux Tr 1차 차단기 조작시험","2020-10-07 10:00","2020-10-07 14:00","2020-10-07 10:00","2020-10-07 14:00","연속"]
[325,"강원","직할","철원화천#1 T/L","화천S/S 드라이비트 보수공사","외벽드라이비트 탈락 및 파손 보수","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[326,"강원","직할","철원화천#2 T/L","화천S/S 드라이비트 보수공사","외벽드라이비트 탈락 및 파손 보수","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[327,"강원","직할","화천화천HP#2 T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","화천S/S 154kV 화천-화천HP #2 T/L 차단기 조작시험, LA 보통점검","2020-10-07 10:00","2020-10-08 18:00","취소","취소","매일"]
[328,"강원","직할","화천H/P 154kV #1 BUS","20~21 강원본부 직할 변전정비 총액공사","#4M.Tr 2차 DS 보통점검","2020-10-22 09:00","2020-10-22 14:00","2020-10-22 09:00","2020-10-22 14:00","연속"]
[329,"강원","직할","화천H/P 154kV #2 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #2 DS 보통점검 ○ #2 BUS CVT 보통점검","2020-10-07 14:00","2020-10-07 18:00","2020-10-07 14:00","2020-10-07 18:00","연속"]
[330,"강원","직할","화천H/P 154kV CB 6433","2020년 하반기 강원 직할 154kV GIS 정밀점검","154kV CB 정밀점검","2020-10-22 09:00","2020-10-24 18:00","2020-10-22 09:00","2020-10-24 18:00","연속"]
[331,"강원","직할","화천H/P 154kV #2 BUS","20~21 강원본부 직할 변전정비 총액공사","#4M.Tr 2차 DS 보통점검","2020-10-22 14:00","2020-10-22 18:00","2020-10-22 14:00","2020-10-22 18:00","연속"]
[332,"강원","직할","화천화천HP#1 T/L","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1, 2 DS 보통점검","2020-10-07 10:00","2020-10-07 18:00","취소","취소","연속"]
[333,"강원","직할","양구화천HP#2 T/L","2020년 하반기 장기 미동작 차단기 조작시험","화천HP 154kV 양구-화천H/P #2 T/L 차단기 조작시험","2020-10-05 10:00","2020-10-05 18:00","2020-10-05 10:00","2020-10-05 18:00","연속"]
[334,"강원","직할","화천H/P 154kV #1 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1 DS 보통점검 ○ #1 BUS CVT 보통점검","2020-10-07 10:00","2020-10-07 14:00","2020-10-07 10:00","2020-10-07 14:00","연속"]
[335,"강원","태백","신제천영월CC#2 T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48) 0.735km 교체","2020-10-07 08:00","2020-10-08 18:00","2020-10-07 08:00","2020-10-08 18:00","연속"]
[336,"강원","태백","동영월영월CC T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48) 14.46km 교체 - 학공장애표시구 50개 철거 및 설치","2020-10-07 08:00","2020-10-18 18:00","2020-10-07 08:00","2020-10-18 18:00","연속"]
[337,"강원","태백","태백삼척GP#1 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거","2020-10-18 08:00","2020-10-25 18:00","2020-10-18 08:00","2020-10-25 18:00","연속"]
[338,"강원","태백","태백삼척GP#2 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거(※ 태백-삼척GP #2 T/L 의 경우 10.11(일) 당일 No.80에서 점퍼분리 후 복구시행)","2020-10-18 08:00","2020-10-25 18:00","2020-10-18 08:00","2020-10-25 18:00","연속"]
[339,"충북","직할","삼죽광혜원 T/L","20~21년도 직할 변전정비회사 총액공사","장기사용 배전반 대체 및 GIS 보통점검","2020-10-26 09:00","2020-10-29 18:00","2020-10-26 09:00","2020-10-29 18:00","연속"]
[340,"충북","직할","사리초정#2 T/L","'20~21년 직할 변전정비회사 총액공사","LA 대체","2020-10-29 10:00","2020-10-29 18:00","취소","취소","연속"]
[341,"충북","직할","사리초정#1 T/L","154kV 사리-초정T/L OPGW 시설공사","154kV 사리-초정T/L OPGW 13km 시설","2020-10-14 09:00","2020-10-21 18:00","2020-10-13 09:00","2020-10-20 18:00","연속"]
[342,"충북","직할","음성사리 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","154kV 풍동-음성#2T/L 사선애자진단에 따른 안전이격 확보","2020-10-08 09:00","2020-10-09 18:00","취소","취소","매일"]
[343,"충북","직할","신진천S/S 154kV CB 6300","20년도 충북본부 직할 154kV GIS 정밀점검공사","#3 BUS TIE GIS 보통+조작부 정밀점검","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[344,"충북","직할","진천광혜원#1 T/L","진천S/S 154kV BUS SEC 설치공사","- 154kV GIS 3CCT 설치 (#60-61, 65-66 BUS SEC, #6200 BUS TIE) - 154kV GIS 1CCT 이설 (#6100 BUS TIE) - 154kV PT Bay 설치 (#61-66 PT)","2020-10-31 09:00","2020-11-06 18:00","2020-10-31 09:00","2020-11-06 18:00","연속"]
[345,"충북","직할","진천덕산#1 T/L","진천S/S 154kV BUS SEC 설치공사","- 154kV GIS 3CCT 설치 (#60-61, 65-66 BUS SEC, #6200 BUS TIE) - 154kV GIS 1CCT 이설 (#6100 BUS TIE) - 154kV PT Bay 설치 (#61-66 PT)","2020-10-13 09:00","2020-10-20 18:00","2020-10-13 09:00","2020-10-20 18:00","연속"]
[346,"충북","직할","진천덕산#2 T/L","진천S/S 154kV BUS SEC 설치공사","- 154kV GIS 3CCT 설치 (#60-61, 65-66 BUS SEC, #6200 BUS TIE) - 154kV GIS 1CCT 이설 (#6100 BUS TIE) - 154kV PT Bay 설치 (#61-66 PT)","2020-10-22 09:00","2020-10-31 18:00","2020-10-22 09:00","2020-10-31 18:00","연속"]
[347,"충북","직할","진천S/S 154kV CB 6100","진천S/S 154kV BUS SEC 설치공사","- 154kV GIS 3CCT 설치 (#60-61, 65-66 BUS SEC, #6200 BUS TIE) - 154kV GIS 1CCT 이설 (#6100 BUS TIE) - 154kV PT Bay 설치 (#61-66 PT)","2020-10-18 09:00","2020-11-10 18:00","2020-10-18 09:00","2020-11-10 18:00","연속"]
[348,"충북","청주","국사봉명#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-10-24 07:00","2020-10-25 18:00","2020-10-24 07:00","2020-10-25 18:00","연속"]
[349,"충북","청주","국사봉명#1 T/L","154kV 오창-봉명구간 OPGW 시설공사","○ 공사구간 : 오창S/S ∼ 국사S/S ∼ 국사-봉명 11호(오송-북청주 32호) ○ 공사내용 : 가공지선 ACSR 97㎟ 철거 및 OPGW 100㎟ 시설 ○ 시 공 사 : 한전KDN, 시공관리책임자 : 백승갑 (H.P:010-4141-1352)","2020-10-24 08:00","2020-10-25 18:00","2020-10-24 08:00","2020-10-25 18:00","연속"]
[350,"충북","청주","국사봉명#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 국사-봉명T/L No.24 철탑1기 교체","2020-10-17 07:00","2020-10-18 18:00","2020-10-17 07:00","2020-10-18 18:00","연속"]
[351,"충북","청주","오창국사#2 T/L","20년 하반기 청주전력지사 170kV GIS 정밀점검공사","국사S/S 오창국사#2T/L CB 정밀점검","2020-10-19 09:30","2020-10-20 18:00","2020-10-19 09:30","2020-10-20 18:00","연속"]
[352,"충북","청주","남청주오송#1 T/L","2020-2021년 청주전력지사 송전정비회사 총액공사","1. 항공장애표시구 교체 - No.7~9, 14~15, 18~19, 21~22, 26~27 2. 지지애자 교체 - 남청주S/T, No.2, 3, 4, 5, 26","2020-10-24 08:00","2020-10-24 18:00","2020-10-24 08:00","2020-10-24 18:00","연속"]
[353,"충북","청주","남청주오송#2 T/L","2020-2021년 청주전력지사 송전정비회사 총액공사","1. 항공장애표시구 교체 - No.7~9, 14~15, 18~19, 21~22, 26~27 2. 지지애자 교체 - 남청주S/T, No.23, 24","2020-10-25 08:00","2020-10-25 18:00","2020-10-25 08:00","2020-10-25 18:00","연속"]
[354,"충북","청주","북청주봉명#2 T/L","20년 하반기 청주전력지사 170kV GIS 정밀점검공사","봉명S/S 북청주봉명#2T/L CB 정밀점검","2020-10-12 09:30","2020-10-13 18:00","2020-10-17 09:30","2020-10-18 18:00","연속"]
[355,"충북","청주","오송북청주#1 T/L","154kV 오창-봉명구간 OPGW 시설공사","○ 공사구간 : 오창S/S ∼ 국사S/S ∼ 국사-봉명 11호(오송-북청주 32호) ○ 공사내용 : 가공지선 ACSR 97㎟ 철거 및 OPGW 100㎟ 시설 ○ 시 공 사 : 한전KDN, 시공관리책임자 : 백승갑 (H.P:010-4141-1352)","2020-10-26 08:00","2020-10-27 18:00","취소","취소","연속"]
[356,"충북","청주","오송북청주#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-24 07:00","2020-10-25 18:00","2020-10-24 07:00","2020-10-25 18:00","연속"]
[357,"충북","청주","오송북청주#2 T/L","154kV 오송-북청주 등 2개T/L EBA PD단자 집합반 설치공사","EBA PD단자 집합반 설치","2020-10-17 09:00","2020-10-18 18:00","2020-10-17 09:00","2020-10-18 18:00","연속"]
[358,"충북","청주","오송북청주#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-17 07:00","2020-10-18 18:00","2020-10-17 07:00","2020-10-18 18:00","연속"]
[359,"충북","청주","오창국사#1 T/L","154kV 오창-봉명구간 OPGW 시설공사","○ 공사구간 : 오창S/S ∼ 국사S/S ∼ 국사-봉명 11호(오송-북청주 32호) ○ 공사내용 : 가공지선 ACSR 97㎟ 철거 및 OPGW 100㎟ 시설 ○ 시 공 사 : 한전KDN, 시공관리책임자 : 백승갑 (H.P:010-4141-1352)","2020-10-24 08:00","2020-10-27 18:00","2020-10-24 08:00","2020-10-27 18:00","연속"]
[360,"충북","충주","금왕남음성#1 T/L","2020~21년 직할 송전정비회사 총액공사","아킹혼설치(29기), 추락방지시설설치(58,59)","2020-10-13 08:00","2020-10-17 18:00","2020-10-13 08:00","2020-10-17 18:00","연속"]
[361,"충북","충주","금왕남음성#2 T/L","남음성S/S #1M.Tr 증설공사","#1M.Tr 1차 GIS 도킹관련 감압 및 무부하 가압(65BUS)","2020-10-19 09:00","2020-10-22 18:00","2020-10-19 09:00","2020-10-22 18:00","연속"]
[362,"충북","충주","금왕남음성#2 T/L","남음성S/S #1M.Tr 증설공사","#1M.Tr 1차 GIS 도킹관련 감압 및 무부하 가압(60BUS)","2020-10-26 09:00","2020-10-29 18:00","2020-10-26 09:00","2020-10-29 18:00","연속"]
[363,"충북","충주","단양영월CC#1 T/L","2020-2021년 송전정비회사 총액공사","장기사용 애자교체 (No.59,65)","2020-10-07 07:00","2020-10-07 18:00","취소","취소","연속"]
[364,"충북","충주","문경단양 T/L","154kV 단양T/L No.9~11 안전이격확보공사","철탑 1기 교체 (No.10)","2020-10-12 07:00","2020-10-12 18:00","2020-10-12 07:00","2020-10-12 18:00","연속"]
[365,"충북","충주","점촌단양 T/L","154kV 단양T/L No.9~11 안전이격확보공사","철탑 1기 교체 (No.10)","2020-10-13 07:00","2020-10-16 12:00","2020-10-13 07:00","2020-10-16 12:00","연속"]
[366,"충북","충주","문경단양 T/L","154kV 단양T/L No.9~11 안전이격확보공사","철탑 1기 교체 (No.10)","2020-10-16 13:00","2020-10-19 18:00","2020-10-16 13:00","2020-10-19 18:00","연속"]
[367,"충북","충주","신제천제천#2 T/L","20-21년 충주전력지사 변전정비 총액공사","신제천S/S 신제천-제천#2T/L GIS 보통점검 제천S/S 신제천-제천#2T/L GIS 보통점검","2020-10-23 10:00","2020-10-23 18:00","취소","취소","연속"]
[368,"충북","충주","신충주음성#2 T/L","2020~21년 직할 송전정비회사 총액공사","불량애자교체(5기), 추락방지시설(2기)설치","2020-10-22 08:00","2020-10-24 18:00","2020-10-22 08:00","2020-10-24 18:00","매일"]
[369,"충북","충주","왕암가남#2 T/L","154kV 왕암-가남T/L 안전이격 확보공사","철탑이설(119호, 120호), 전력선교체 1경간(No.119~120호간)","2020-10-31 08:00","2020-11-03 18:00","취소","취소","연속"]
[370,"충북","충주","왕암가남#1 T/L","154kV 왕암-가남T/L 안전이격 확보공사","철탑이설(119호, 120호), 전력선교체 1경간(No.119~120호간)","2020-10-22 08:00","2020-10-30 18:00","취소","취소","연속"]
[371,"충북","충주","왕암가남#2 T/L","154kV 왕암-가남T/L 안전이격 확보공사","철탑이설(119호, 120호), 전력선교체 1경간(No.119~120호간)","2020-10-19 08:00","2020-10-21 18:00","취소","취소","연속"]
[372,"충북","충주","신제천왕암#1 T/L","20-21년 충주전력 변전정비회사 총액공사","변전소 인출 월부싱 코로나 및 과열관련 부싱점검","2020-10-06 13:00","2020-10-06 18:00","취소","취소","연속"]
[373,"충북","충주","신제천왕암#2 T/L","20-21년 충주전력 변전정비회사 총액공사","변전소 인출 월부싱 코로나 및 과열관련 부싱점검","2020-10-06 08:00","2020-10-06 13:00","취소","취소","연속"]
[374,"충북","충주","음성금왕#2 T/L","2020~21년 직할 송전정비회사 총액공사","전선교체공사(2경간),아킹혼설치(4회선47기), 불량애자교체(3기)","2020-10-13 08:00","2020-10-28 18:00","2020-10-13 08:00","2020-10-28 18:00","매일"]
[375,"충북","충주","음성금왕#1 T/L","2020~21년 직할 송전정비회사 총액공사","전선교체공사(2경간), 애자교체, 추락방지시설(2기)설치","2020-10-29 08:00","2020-10-31 18:00","2020-10-29 08:00","2020-10-31 18:00","연속"]
[376,"충북","충주","제천영월#2 T/L","2020-2021년 송전정비회사 총액공사","장기사용 애자교체 (No.44-1, 49)","2020-10-06 07:00","2020-10-06 18:00","취소","취소","연속"]
[377,"충북","충주","제천영월#1 T/L","2020-2021년 송전정비회사 총액공사","장기사용 애자교체 (No.44-1)","2020-10-05 07:00","2020-10-05 18:00","취소","취소","연속"]
[378,"충북","충주","충주풍동 T/L","154kV 충주-음성-사리구간 OPGW 시설공사","154kV 충주-음성-사리구간 가공지선 철거 및 OPGW 60km 시설","2020-10-12 08:00","2020-10-12 18:00","2020-10-12 08:00","2020-10-12 18:00","연속"]
[379,"충북","충주","충주S/S 154kV SEC CB 60610","2020년 충주전력지사 170kV GIS 정밀점검","충주S/S #60-#61 SEC GIS 정밀점검","2020-10-28 09:00","2020-10-29 18:00","취소","취소","연속"]
[380,"충북","충주","풍동음성#2 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","사선애자진단 (중각도철탑 11기)","2020-10-08 09:00","2020-10-12 18:00","취소","취소","매일"]
[381,"충북","청주","국사봉명#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-09 07:00","2020-10-11 18:00","2020-10-09 07:00","2020-10-11 18:00","연속"]
[382,"충북","청주","오송북청주#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-09 07:00","2020-10-11 18:00","2020-10-10 09:00","2020-10-11 18:00","연속"]
[383,"충북","청주","국사봉명#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-03 07:00","2020-10-04 18:00","2020-10-03 07:00","2020-10-04 18:00","연속"]
[384,"충북","청주","오송북청주#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-03 07:00","2020-10-04 18:00","2020-10-03 07:00","2020-10-04 18:00","연속"]
[385,"충북","청주","국사봉명#1 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-31 07:00","2020-10-31 18:00","2020-10-31 07:00","2020-10-31 18:00","연속"]
[386,"충북","청주","오송북청주#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","철탑1기 교체(No.24)","2020-10-31 07:00","2020-10-31 18:00","2020-10-31 07:00","2020-10-31 18:00","연속"]
[387,"대전충남","대전","팔봉두마#1 T/L","[송전]154kV 신계룡-두마#1T/L 정밀점검","[송전]154kV 팔봉-두마#1T/L(병가) 정밀점검","2020-10-06 07:30","2020-10-07 18:00","2020-10-06 07:30","2020-10-07 18:00","매일"]
[388,"대전충남","대전","신계룡두마#2 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-19 07:00","2020-10-23 18:00","2020-10-19 07:00","2020-10-23 18:00","연속"]
[389,"대전충남","대전","신계룡두마#2 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-19 07:00","2020-10-21 18:00","취소","취소","매일"]
[390,"대전충남","대전","신계룡두마#2 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-12 07:00","2020-10-16 18:00","2020-10-12 07:00","2020-10-16 18:00","연속"]
[391,"대전충남","대전","신계룡두마#1 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-19 07:00","2020-10-21 18:00","2020-10-19 07:00","2020-10-21 18:00","매일"]
[392,"대전충남","대전","신계룡은진#2 T/L","154kV 신계룡-두마T/L OPGW 증설공사","신계룡S/S ~ 두마S/S 간 가공지선(ACSR 97SQ)를 OPGW/100SQ로 변경","2020-10-12 07:00","2020-10-16 18:00","2020-10-12 07:00","2020-10-16 18:00","연속"]
[393,"대전충남","서산","신당진당진#2 T/L","20년 서산P/O 변전정비 총액공사","당진S/S 154kV 신당진-당진#2T/L GIS(657) 보통점검","2020-10-20 10:00","2020-10-20 18:00","취소","취소","연속"]
[394,"대전충남","서산","신당진당진#1 T/L","154kV 대산-석문등 6개T/L 성능저하 애자교체 공사","애자교체 공사 : No.4(1기)","2020-10-21 08:00","2020-10-21 12:00","2020-10-21 08:00","2020-10-21 12:00","연속"]
[395,"대전충남","서산","신당진당진#2 T/L","154kV 대산-석문등 6개T/L 성능저하 애자교체 공사","애자교체 공사 : 신당진S/T, No.3,5,6(4기)","2020-10-20 08:00","2020-10-20 18:00","2020-10-20 08:00","2020-10-20 18:00","연속"]
[396,"대전충남","서산","대산석문#1 T/L","대산S/S 154kV 현대케미칼#1,2T/L GIS 증설공사","대산S/S 154kV 현대케미칼#1,2T/L GIS 증설공사 관련 안전이격 확보","2020-10-19 08:00","2020-10-20 18:00","2020-10-19 08:00","2020-10-20 18:00","매일"]
[397,"대전충남","서산","대산석문#2 T/L","154kV 대산-석문 등 6개T/L 성능저하 애자교체공사","애자 교체 공사 : No.18,43(2기) 작업시간 : 14:00~18:00","2020-10-28 14:00","2020-10-28 18:00","2020-10-28 14:00","2020-10-28 18:00","연속"]
[398,"대전충남","서산","대산석문#1 T/L","대산S/S 154kV 현대케미칼#1,2T/L GIS 증설공사","대산S/S 154kV 현대케미칼#1,2T/L GIS 증설공사 관련 안전이격 확보","2020-10-26 08:00","2020-10-27 18:00","2020-10-26 08:00","2020-10-27 18:00","매일"]
[399,"대전충남","서산","석문당진화력#2 T/L","154kV 대산-석문 등 6개T/L 성능저하 애자교체공사","애자 교체 공사 : No.18(1기)","2020-10-23 08:00","2020-10-23 18:00","2020-10-23 08:00","2020-10-23 18:00","연속"]
[400,"대전충남","서산","당진송악#2 T/L","154당진-송악T/L 추락방지장치설치","No.20,21:추락방지장치설치","2020-10-15 08:00","2020-10-15 18:00","2020-10-15 08:00","2020-10-15 18:00","연속"]
[401,"대전충남","서산","당진송악#1 T/L","154당진-송악T/L 추락방지장치설치","No.20,21:추락방지장치설치","2020-10-16 08:00","2020-10-16 18:00","2020-10-16 08:00","2020-10-16 18:00","연속"]
[402,"대전충남","서산","신당진서산#2 T/L","20년 장기 미동작 차단기 조작시험","신당진S/S 154kV 신당진서산#2T/L 667 CB 조작시험","2020-10-07 10:00","2020-10-07 14:00","취소","취소","연속"]
[403,"대전충남","서산","신당진서산#1 T/L","154kV 대산-석문등 6개T/L 성능저하 애자교체 공사","애자교체 공사 : 서산S/T No.28,60(3기)","2020-10-21 12:00","2020-10-21 18:00","2020-10-21 12:00","2020-10-21 18:00","연속"]
[404,"대전충남","서산","태안태안화력 T/L","154kV 태안-태안화력T/L 성능저하 애자교체 및 이도조정 공사","애자교체 공사 : No.9(1기) 이도조정 공사 : No.33-34,34-36,40-42,47-48(4개소)","2020-10-22 08:00","2020-10-22 18:00","2020-10-22 08:00","2020-10-22 18:00","연속"]
[405,"대전충남","서산","서산태안 T/L","20년 장기 미동작 차단기 조작시험","태안S/S 154kV 서산태안T/L 647 CB 조작시험","2020-10-09 10:00","2020-10-09 14:00","2020-10-09 10:00","2020-10-09 14:00","연속"]
[406,"대전충남","서산","합덕송악#2 T/L","154kV 합덕-송악#2T/L 애자교체 및 추락방지장치 설치 공사","애자교체 공사 : No.35,47(2기) 추락방지장치 설치공사 : No.20,21(2기)","2020-10-16 08:00","2020-10-19 18:00","2020-10-16 08:00","2020-10-19 18:00","매일"]
[407,"대전충남","서산","합덕송악#1 T/L","154kV 합덕-송악#1T/L 애자교체 및 추락방지장치 설치 공사","애자교체 공사 : No.35(1기) 추락방지장치 설치공사 : No.20,21(2기)","2020-10-14 08:00","2020-10-15 18:00","2020-10-14 08:00","2020-10-15 18:00","매일"]
[408,"대전충남","세종","신풍공주#1 T/L","154kV 신풍-공주T/L 현수애자교체 및 보강공사","[송전] 신풍-공주#1T/L 현수애자 교체 및 애자련보강 - No.1-2,1-3,1-14, 공주S/T(현수애자교체) * 4회선(1-1~1-14) 구간(상단:신풍-공주#1, 하단:청양-신풍#2)","2020-10-05 07:00","2020-10-07 12:00","2020-10-05 07:00","2020-10-07 12:00","연속"]
[409,"대전충남","세종","신풍공주#2 T/L","154kV 신풍-공주T/L 현수애자교체 및 보강공사","[송전] 신풍-공주#2T/L 현수애자 교체 및 애자련보강 - No.1-1.1-7.53.73.공주S/T(현수애자교체) * 4회선(1-1~1-14) 구간(상단:신풍-공주#2, 하단:청양-신풍#1)","2020-10-07 12:00","2020-10-09 18:00","2020-10-07 12:00","2020-10-09 18:00","연속"]
[410,"대전충남","세종","덕진대화#1 T/L","154kV 덕진-대화T/L 현수애자교체 및 보강공사","[송전] 덕진-대화#1T/L 애자련보강 - No.10호(1련 - 2련)","2020-10-12 07:00","2020-10-12 12:00","2020-10-12 07:00","2020-10-12 12:00","연속"]
[411,"대전충남","세종","덕진대화#2 T/L","154kV 덕진-대화T/L 현수애자교체 및 보강공사","[송전] 덕진-대화#2T/L 현수애자 교체 및 애자련보강 - No.10호(1련 - 2련) - No.17호(현수 - 폴리머애자교체) - No.21호(현수애자교체)","2020-10-12 12:00","2020-10-13 18:00","2020-10-12 12:00","2020-10-13 18:00","연속"]
[412,"대전충남","세종","둔곡송강#1 T/L","154kV 둔곡-송강T/L 현수애자교체 및 보강공사","[송전] 둔곡-송강#1T/L 현수애자 교체 및 애자련보강 - No.14호(현수애자교체)","2020-10-28 07:00","2020-10-28 12:00","2020-10-28 07:00","2020-10-28 12:00","연속"]
[413,"대전충남","세종","둔곡송강#2 T/L","154kV 둔곡-송강T/L 현수애자교체 및 보강공사","[송전] 둔곡-송강#2T/L 현수애자 교체 및 애자련보강 - No.5호(현수애자교체)","2020-10-28 12:00","2020-10-28 18:00","2020-10-28 12:00","2020-10-28 18:00","연속"]
[414,"대전충남","세종","부강신탄진 T/L","154kV 부강-신탄진T/L 현수애자교체 및 보강공사","[송전] 부강-신탄진T/L 현수애자 교체 및 애자련보강 - No.6,56호(현수애자교체)","2020-10-29 07:00","2020-10-29 18:00","2020-10-29 07:00","2020-10-29 18:00","연속"]
[415,"대전충남","세종","세종둔곡#2 T/L","154kV 세종-둔곡 C/H No.1 EBA 과열개소 조치","154kV 세종-둔곡 C/H No.1 EBA 과열개소 조치","2020-10-23 09:00","2020-10-23 18:00","2020-10-23 09:00","2020-10-23 18:00","연속"]
[416,"대전충남","세종","세종둔곡#1 T/L","154kV 세종-둔곡 C/H No.1 EBA 과열개소 조치","154kV 세종-둔곡 C/H No.1 EBA 과열개소 조치","2020-10-22 09:00","2020-10-22 18:00","2020-10-22 09:00","2020-10-22 18:00","연속"]
[417,"대전충남","세종","조치원월산 T/L","[변전]'20년 170kV GIS 정밀점검공사","○170kV GIS 정밀점검공사","2020-10-07 07:00","2020-10-08 18:00","2020-10-07 07:00","2020-10-08 18:00","연속"]
[418,"대전충남","세종","천안전의#1 T/L","154kV 천안-전의T/L 현수애자교체 및 보강공사","[송전] 천안-전의#1T/L 현수애자 교체 및 애자련보강 - No.1,2호(현수애자교체)","2020-10-24 07:00","2020-10-24 18:00","2020-10-31 07:00","2020-10-31 18:00","연속"]
[419,"대전충남","세종","서세종조치원 T/L","[변전]'20년 170kV GIS 정밀점검공사","○170kV GIS 정밀점검공사","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[420,"대전충남","아산","둔포석곡#2 T/L","154kV 둔포-석곡#2T/L 피뢰기 절연열화 측정","154kV 둔포-석곡 #2T/L 피뢰기 절연열화 측정","2020-10-06 09:00","2020-10-06 18:00","2020-10-06 09:00","2020-10-06 18:00","연속"]
[421,"대전충남","아산","둔포석곡#1 T/L","154kV 둔포-석곡#1T/L 피뢰기 절연열화측정","154kV 둔포-석곡#1T/L 피뢰기 절연열화 측정","2020-10-05 09:00","2020-10-05 18:00","2020-10-05 09:00","2020-10-05 18:00","연속"]
[422,"대전충남","아산","불당서천안#2 T/L","불당S/S 불당-서천안#2T/L CB 전자변 교체","불당S/S 불당-서천안#2T/L CB 전자변 교체","2020-10-16 09:00","2020-10-16 18:00","취소","취소","연속"]
[423,"대전충남","아산","불당서천안#1 T/L","불당S/S 불당-서천안#1T/L CB 전자변 교체","불당S/S 불당-서천안#1T/L CB 전자변 교체","2020-10-15 09:00","2020-10-15 18:00","취소","취소","연속"]
[424,"대전충남","아산","성거천안#1 T/L","154kV 성거-천안#1T/L EBA 절연유 채유","154kV 성거-천안#1T/L EBA 절연유 채유 및 피뢰기 절연열화 측정","2020-10-08 09:00","2020-10-08 18:00","2020-10-15 09:00","2020-10-15 18:00","연속"]
[425,"대전충남","아산","성거천안#2 T/L","154kV 성거-천안#2T/L EBA 절연유 채유","154kV 성거-천안#2T/L EBA 절연유 채유 및 피뢰기 절연열화 측정","2020-10-09 09:00","2020-10-09 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[426,"대전충남","아산","신탕정S/S 154kV CB 6200","신탕정S/S 345kV #4M.Tr 증설관련 모선보호반 연동시험","신탕정S/S 345kV #4M.Tr 증설관련 모선보호반 연동시험","2020-10-07 14:00","2020-10-07 16:00","2020-10-07 14:00","2020-10-07 16:00","연속"]
[427,"대전충남","아산","신탕정S/S 154kV CB 6100","신탕정S/S 345kV #4M.Tr 증설관련 모선보호반 연동시험","신탕정S/S 345kV #4M.Tr 증설관련 모선보호반 연동시험","2020-10-07 14:00","2020-10-07 16:00","2020-10-07 14:00","2020-10-07 16:00","연속"]
[428,"대전충남","아산","온양풍세#1 T/L","온양,풍세S/S 154kV 온양-풍세#1T/L PNL 교체","온양,풍세S/S 154kV 온양-풍세#1T/L PNL 교체","2020-10-05 09:00","2020-10-08 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[429,"대전충남","아산","장재천안#1 T/L","[송전]154kV 장재-천안#1,2T/L No.24~25 지중화공사","천안시 청당지구 지중화 사업요청에 의한 154kV 장재-천안#1,2T/L No.24~25 일부구간 지중화 (0.573km)","2020-10-29 08:00","2020-12-06 18:00","2020-10-29 08:00","2020-12-06 18:00","연속"]
[430,"대전충남","직할","덕진대화#1 T/L","[송전]154kV 옥산-부여 등 3개T/L 자기애관 교체공사","○ 비표준형 및 표준형 EBA 자기애관 → 폴리머애관 30상 교체","2020-10-19 08:00","2020-10-30 18:00","2020-10-19 08:00","2020-10-30 18:00","연속"]
[431,"대전충남","직할","동대전신탄진#2 T/L","[송전]154kV 동대전-신탄진T/L 안전이격거리 확보공사","○ 철탑설치/철거 : No.7,8,13 ○ 철탑보강 : No.14 ○ 전력선교체 : No.6~9, 11~14(HSTACIR/AW)","2020-10-19 09:00","2020-10-27 18:00","2020-10-19 09:00","2020-10-27 18:00","연속"]
[432,"대전충남","직할","동대전신탄진#1 T/L","[송전]154kV 동대전-신탄진T/L 안전이격거리 확보공사","○ 철탑설치/철거 : No.7,8,13 ○ 철탑보강 : No.14 ○ 전력선교체 : No.6~9, 11~14(HSTACIR/AW)","2020-10-19 09:00","2020-10-31 18:00","2020-10-19 09:00","2020-10-31 18:00","연속"]
[433,"대전충남","직할","송강신일#2 T/L","154kV 송강-신일#2T/L OF Cable 절연유채유","154kV 송강-신일#2T/L OF Cable 절연유채유","2020-10-26 09:00","2020-10-26 18:00","2020-10-26 09:00","2020-10-26 18:00","연속"]
[434,"대전충남","직할","신탄진대청HP T/L","154kV 신탄진-대청HP T/L 현수애자교체 및 보강공사","[송전] 신탄진-대청HP T/L 현수애자 교체 및 애자련보강 - No.7호(현수애자교체)","2020-10-30 07:00","2020-10-30 18:00","2020-10-30 07:00","2020-10-30 18:00","연속"]
[435,"대전충남","청양","청양신풍#1 T/L","[송전] 154kV 청양-은하 등 2개T/L 접속개소제거 전선교체공사","154kV 청양-신풍#2T/L 접속개소제거 전선교체공사 - No.32~34 상단 2가닥 - No.40~42 하단 2가닥","2020-10-14 07:00","2020-10-15 18:00","취소","취소","연속"]
[436,"대전충남","청양","청양신풍#2 T/L","[송전] 154kV 청양-은하 등 2개T/L 접속개소제거 전선교체공사","154kV 청양-신풍#2T/L 접속개소제거 전선교체공사 - No.32~34 상단 2가닥 - No.40~42 하단 2가닥","2020-10-12 07:00","2020-10-13 18:00","취소","취소","연속"]
[437,"대전충남","청양","동군산장항#2 T/L","[송전]154kV 옥산-장항T/L 불량애자교체공사(병가)","[송전]154kV 옥산-장항T/L 불량애자교체공사(병가) - No.3~70 (19기, 1,096장)","2020-10-14 08:00","2020-10-14 18:00","2020-10-20 08:00","2020-10-20 18:00","연속"]
[438,"대전충남","청양","옥산장항#2 T/L","154kV 장항S/S #4M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치 관련 안전이격확보","2020-10-26 09:00","2020-10-27 18:00","취소","취소","매일"]
[439,"대전충남","청양","옥산장항#2 T/L","154kV 장항S/S #4M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치 관련 안전이격확보","2020-10-19 09:00","2020-10-20 18:00","취소","취소","매일"]
[440,"대전충남","청양","장항S/S 154kV #2 BUS","154kV 장항S/S #4M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치 및 기타부대공사","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","연속"]
[441,"대전충남","청양","동군산장항#1 T/L","[송전]154kV 옥산-장항T/L 불량애자교체공사(병가)","[송전]154kV 옥산-장항T/L 불량애자교체공사(병가) - No.3~70 (19기, 1,096장)","2020-10-15 08:00","2020-10-15 18:00","2020-10-21 08:00","2020-10-21 18:00","연속"]
[442,"대전충남","청양","장항S/S 154kV #1 BUS","154kV 장항S/S #4M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치 및 기타부대공사","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[443,"대전충남","청양","청양신풍#1 T/L","154kV 청양-신풍T/L 현수애자교체 및 보강공사","[송전] 청양-신풍#1T/L 현수애자 교체 및 애자련보강 - No.49,56,62호(현수애자교체) * 4회선(49~62) 구간(상단:신풍-공주#2, 하단:청양-신풍#1)","2020-10-07 12:00","2020-10-09 18:00","2020-10-07 12:00","2020-10-09 18:00","연속"]
[444,"대전충남","청양","청양신풍#2 T/L","154kV 청양-신풍T/L 현수애자교체 및 보강공사","[송전] 청양-신풍#2T/L 현수애자 교체 및 애자련보강 - No.60,61호(현수애자교체) * 4회선(49~62) 구간(상단:신풍-공주#1, 하단:청양-신풍#2)","2020-10-05 07:00","2020-10-07 12:00","2020-10-05 07:00","2020-10-07 12:00","연속"]
[445,"대전충남","청양","해미홍성 T/L","홍성S/S 해미-홍성T/L GIS 보통점검","홍성S/S 해미-홍성T/L GIS 보통점검","2020-10-07 09:00","2020-10-07 18:00","2020-10-07 09:00","2020-10-07 18:00","연속"]
[446,"전북","군산","비응군장#1 T/L","비응S/S 170kV GIS 제작사 부분방전 하자보수공사","GIS 이음발생 하자보수 2DS 이음개소 하자보수","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[447,"전북","군산","새만금비응#1 T/L","비응S/S 170kV GIS 제작사 부분방전 하자보수공사","GIS 이음발생 하자보수 2DS 이음개소 하자보수","2020-10-19 09:00","2020-10-23 18:00","2020-10-19 09:00","2020-10-23 18:00","연속"]
[448,"전북","군산","비응군장#2 T/L","비응S/S 154kV GIS 제작사 부분방전 관련 하자보수공사","차단부 부분방전 하자보수 2DS 이음개소 하자보수","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[449,"전북","군산","새만금비응#2 T/L","비응S/S 154kV GIS 제작사 부분방전 관련 하자보수공사","차단부 부분방전 하자보수 2DS 이음개소 하자보수","2020-10-12 09:00","2020-10-16 18:00","2020-10-12 09:00","2020-10-16 18:00","연속"]
[450,"전북","군산","새만금소룡#2 T/L","'20년 군산P/O 170kV GIS 정밀점검공사","새만금S/S 154kV 새만금-소룡#2T/L GIS 정밀점검","2020-10-21 09:00","2020-10-22 18:00","2020-10-21 09:00","2020-10-22 18:00","연속"]
[451,"전북","군산","새만금소룡#1 T/L","20년 군산P/O 170kV GIS 정밀점검공사(무부하가압)","새만금S/S 154kV #66-#67 SEC GIS 정밀점검 무부하가압","2020-10-20 14:00","2020-10-20 16:00","2020-10-20 14:00","2020-10-20 16:00","연속"]
[452,"전북","군산","새만금소룡#2 T/L","20년 군산P/O 170kV GIS 정밀점검공사(무부하가압)","새만금S/S 154kV #61-62 SEC GIS 정밀점검 무부하가압","2020-10-15 14:00","2020-10-15 16:00","2020-10-15 14:00","2020-10-15 16:00","연속"]
[453,"전북","군산","새만금소룡#1 T/L","20년 군산P/O 170kV GIS 정밀점검공사(무부하가압)","새만금S/S 154kV #61-#67 BUS-TIE GIS 정밀점검 무부하가압","2020-10-13 14:00","2020-10-13 16:00","2020-10-13 14:00","2020-10-13 16:00","연속"]
[454,"전북","군산","새만금소룡#1 T/L","'20년 군산P/O 170kV GIS 정밀점검공사","새만금S/S 154kV 새만금-소룡#1T/L GIS 정밀점검","2020-10-07 09:00","2020-10-08 18:00","취소","취소","연속"]
[455,"전북","군산","새만금소룡#1 T/L","20년 군산P/O 170kV GIS 정밀점검공사(무부하가압)","새만금S/S 345kV #2M.Tr 2차 GIS 정밀점검 무부하가압용","2020-10-06 14:00","2020-10-06 16:00","취소","취소","연속"]
[456,"전북","군산","새만금비응#2 T/L","'20년 군산P/O 170kV GIS 정밀점검공사","새만금S/S 154kV 새만금-비응#2T/L GIS 정밀점검","2020-10-28 09:00","2020-10-29 18:00","2020-10-28 09:00","2020-10-29 18:00","연속"]
[457,"전북","군산","새만금비응#1 T/L","'20년 군산P/O 170kV GIS 정밀점검공사","새만금S/S 154kV 새만금-비응#1T/L GIS 정밀점검","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[458,"전북","김제","고창영광 T/L","154kV 고창-영광T/L 지지애자교체","154kV 고창-영광T/L 136호(상,중,하)지지애자 교체","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[459,"전북","김제","김제칠보HP T/L","154kV 신김제-전주 등 15개 T/L PD집합반 설치공사","□ 설치대상 : 154kV 신김제-전주 등 15개 T/L, 22개소(C/H) → 전북관내 全 케이블헤드【수직배치형 케이블헤드 제외(설치곤란)】 □ 공사내용 : 케이블헤드 EBA 하단부 UWB센서 및 지상 PD집합반 설치","2020-10-27 09:00","2020-10-27 12:00","2020-10-27 09:00","2020-10-27 12:00","연속"]
[460,"전북","김제","신김제남전주#1 T/L","남전주S/S 신김제-남전주#1T/L RY 교체","남전주S/S 신김제-남전주#1T/L RY 교체","2020-10-12 09:00","2020-10-12 18:00","2020-10-07 09:00","2020-10-07 18:00","연속"]
[461,"전북","김제","백산김제#2 T/L","154kV 백산-김제T/L 송전선로 초기점검","154kV 백산-김제T/L No.21, 24, 28호 초기점검","2020-10-30 08:00","2020-10-30 17:00","2020-10-30 08:00","2020-10-30 17:00","연속"]
[462,"전북","김제","백산김제#1 T/L","154kV 백산-김제T/L 송전선로 초기점검","154kV 백산-김제T/L No.21, 24, 28호 초기점검","2020-10-29 08:00","2020-10-29 17:00","2020-10-29 08:00","2020-10-29 17:00","연속"]
[463,"전북","김제","신김제정공#2 T/L","신김제S/S 노후 170GIS 교체 (교체대상)","장기사용 노후 170GIS 교체공사 (교체대상)","2020-10-05 09:00","2020-10-26 18:00","2020-10-05 09:00","2020-10-29 18:00","연속"]
[464,"전북","김제","신김제S/S 154kV #65 BUS","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#2 BUS 작업)","2020-10-05 09:00","2020-10-10 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[465,"전북","김제","신김제S/S 154kV SEC CB 65660","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#2 BUS 작업)","2020-10-05 09:00","2020-10-10 18:00","2020-10-05 09:00","2020-10-08 18:00","연속"]
[466,"전북","김제","신김제S/S 154kV SEC CB 60610","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#1 BUS 작업)","2020-10-11 09:00","2020-10-18 18:00","2020-10-08 18:00","2020-10-17 18:00","연속"]
[467,"전북","김제","신김제S/S 154kV #60 BUS","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#1 BUS 작업)","2020-10-11 09:00","2020-10-18 18:00","2020-10-08 18:00","2020-10-17 18:00","연속"]
[468,"전북","김제","신김제동전주#1 T/L","신김제S/S 노후 170GIS 교체 (무부하가압)","장기사용 노후 170GIS 교체공사 (무부하가압) (신김제-동전주#1, 신김제-남전주#1 중 둘중 하나선로 무부하가압 가능)","2020-10-10 09:00","2020-10-10 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[469,"전북","김제","신김제S/S 154kV SEC CB 65660","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#2 BUS 작업)","2020-10-19 09:00","2020-10-26 18:00","2020-10-17 18:00","2020-10-29 18:00","연속"]
[470,"전북","김제","신김제S/S 154kV CB 6200","신김제S/S 노후 170GIS 교체 (무부하가압)","신김제S/S 노후 170GIS 교체 (무부하가압)","2020-10-10 09:00","2020-10-10 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[471,"전북","김제","신김제S/S 154kV #66 BUS","신김제S/S 노후 170GIS 교체 (무부하가압)","신김제S/S 노후 170GIS 교체 (무부하가압)","2020-10-10 09:00","2020-10-10 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[472,"전북","김제","신김제남전주#1 T/L","신김제S/S 노후 170GIS 교체 (무부하가압)","장기사용 노후 170GIS 교체공사 (무부하가압) (신김제-동전주#1, 신김제-남전주#1 중 둘중 하나선로 무부하가압 가능)","2020-10-10 09:00","2020-10-10 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[473,"전북","김제","신김제S/S 154kV SEC CB 66670","신김제S/S 노후 170GIS 교체 (무부하가압)","신김제S/S 노후 170GIS 교체 (무부하가압)","2020-10-10 09:00","2020-10-10 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[474,"전북","김제","신김제S/S 154kV CB 6100","신김제S/S 노후 170GIS 교체 (교체대상)","장기사용 노후 170GIS 교체공사 (교체대상)","2020-10-05 09:00","2020-10-26 18:00","2020-10-05 09:00","2020-10-29 18:00","연속"]
[475,"전북","김제","신김제S/S 154kV #65 BUS","신김제S/S 노후 170GIS 교체 ","장기사용 노후 170GIS 교체공사 (#2 BUS 작업)","2020-10-19 09:00","2020-10-26 18:00","2020-10-17 18:00","2020-10-29 18:00","연속"]
[476,"전북","김제","정공정주#1 T/L","154kV 정공-정주T/L 송전선로 지지애자교체","정공-정주T/L 0.01(인출) 상단 지지애자교체","2020-10-15 08:00","2020-10-15 17:00","2020-10-15 08:00","2020-10-15 17:00","연속"]
[477,"전북","김제","정주고창#1 T/L","154kV 정주-고창T/L 초기점검","154kV 정주-고창T/L No.25, 31, 35호 초기점검","2020-10-26 08:00","2020-10-26 17:00","2020-10-26 08:00","2020-10-26 17:00","연속"]
[478,"전북","김제","정주고창#2 T/L","154kV 정주-고창T/L 초기점검","154kV 정주-고창T/L No.25, 31, 35호 초기점검","2020-10-27 08:00","2020-10-27 17:00","2020-10-27 08:00","2020-10-27 17:00","연속"]
[479,"전북","직할","신남원남원#1 T/L","남원S/S 옥외철구설비 GIS화 공사","○ 154kV 신남원-남원#1T/L 선로변경(가공→지중) ○ 154kV GIS 가압 ○ 신남원, 남원S/S 보호배전반 대체 등","2020-10-26 08:00","2020-11-06 18:00","2020-10-26 08:00","2020-11-06 18:00","연속"]
[480,"전북","직할","남원임실#1 T/L","남원S/S 옥외철구설비 GIS화 공사","○ 154kV 남원-임실#1T/L 선로변경(가공→지중) ○ 154kV GIS 가압 ○ 남원, 임실S/S 보호배전반 대체 등","2020-10-26 08:00","2020-11-06 18:00","2020-10-26 08:00","2020-11-06 18:00","연속"]
[481,"전북","직할","무주용담수력 T/L","무주S/S 154kV GIS 교체공사(전문) (무부하가압)","*** 154kV #60BUS 무부하 가압 선로 - 170kV GIS 50kA(1250/2000A) GIS 5CCT 대체 (대상설비 : 금산-무주#1, #2T/L, #1, #2 M.Tr 1차, BUS-TIE, BUS-PT) (무주-용담수력, 무주-진안T/L 둘 중 1개 선로 무부하가압 선로 가능)","2020-10-14 09:00","2020-10-16 18:00","2020-10-27 10:00","2020-10-28 10:00","연속"]
[482,"전북","직할","금산무주#1 T/L","무주S/S 154kV GIS 교체공사(전문) (교체대상)","- 170kV GIS 50kA(1250/2000A) GIS 5CCT 대체 (대상설비 : 금산-무주#1, #2T/L, #1, #2 M.Tr 1차, BUS-TIE, BUS-PT)","2020-10-07 09:00","2020-11-06 18:00","2020-10-20 09:00","2020-11-17 18:00","연속"]
[483,"전북","직할","무주진안 T/L","무주S/S 154kV GIS 교체공사(전문) (무부하가압)","*** 154kV #60BUS 무부하 가압 선로 - 170kV GIS 50kA(1250/2000A) GIS 5CCT 대체 (대상설비 : 금산-무주#1, #2T/L, #1, #2 M.Tr 1차, BUS-TIE, BUS-PT) (무주-용담수력, 무주-진안T/L 둘 중 1개 선로 무부하가압 선로 가능)","2020-10-14 09:00","2020-10-16 18:00","2020-10-27 10:00","2020-10-28 10:00","연속"]
[484,"전북","김제","정공칠보HP T/L","RTU 플로팅 불량관련 회로 변경","RTU 플로팅 불량관련 회로 변경","2020-10-27 13:00","2020-10-27 15:00","2020-10-27 13:00","2020-10-27 15:00","연속"]
[485,"광주전남","강진","강진남창#2 T/L","2020 광주전남 관내 OPGW 항공장애표시구 설치공사","2020 광주전남 관내 OPGW 항공장애표시구 설치공사","2020-10-12 09:00","2020-10-15 18:00","2020-10-12 09:00","2020-10-15 18:00","매일"]
[486,"광주전남","강진","왕곡나주#2 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#2T/L 정밀점검 관련 4회선 병가구간 안전이격거리 확보 - 나주S/S~왕곡S/S, 20기","2020-10-12 13:00","2020-10-12 18:00","2020-10-12 13:00","2020-10-12 18:00","연속"]
[487,"광주전남","강진","신화순나주#1 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#2T/L 정밀점검 관련 4회선 병가구간 안전이격거리 확보 - 신화순S/S~나주S/S, 72기","2020-10-12 08:00","2020-10-12 12:00","2020-10-12 08:00","2020-10-12 12:00","연속"]
[488,"광주전남","강진","왕곡나주#1 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#2T/L 정밀점검 관련 4회선 병가구간 안전이격거리 확보 - 왕곡S/S~나주S/S, 20기","2020-10-05 13:00","2020-10-05 18:00","2020-10-05 13:00","2020-10-05 18:00","연속"]
[489,"광주전남","강진","신화순나주#2 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#1T/L 정밀점검 관련 4회선 병가구간 안전이격거리 확보 - 신화순S/S~나주S/S, 72기","2020-10-05 08:00","2020-10-05 12:00","2020-10-05 08:00","2020-10-05 12:00","연속"]
[490,"광주전남","강진","남창해남CS#2 T/L","'20-21년 강진전력지사 송전정비회사 총액공사","96년 상반기 이전 성능저하 점퍼지지애자 교체 - 고정형 폴리머 점퍼지지애자 교체 32련","2020-10-15 08:00","2020-10-19 18:00","2020-10-15 08:00","2020-10-19 18:00","매일"]
[491,"광주전남","강진","남창해남CS#1 T/L","'20-21년 강진전력지사 송전정비회사 총액공사","96년 상반기 이전 성능저하 점퍼지지애자 교체 - 고정형 폴리머 점퍼지지애자 교체 32련","2020-10-12 08:00","2020-10-14 18:00","2020-10-12 08:00","2020-10-14 18:00","매일"]
[492,"광주전남","강진","신강진대불#2 T/L","'20-21년 강진전력지사 송전정비회사 총액공사","96년 상반기 이전 성능저하 점퍼지지애자 교체 - 고정형 폴리머 점퍼지지애자 교체 27련","2020-10-07 08:00","2020-10-09 18:00","2020-10-21 08:00","2020-10-22 18:00","매일"]
[493,"광주전남","강진","신강진대불#1 T/L","'20-21년 강진전력지사 송전정비회사 총액공사","96년 상반기 이전 성능저하 점퍼지지애자 교체 - 고정형 폴리머 점퍼지지애자 교체 27련","2020-10-05 08:00","2020-10-06 18:00","2020-10-19 08:00","2020-10-20 18:00","매일"]
[494,"광주전남","강진","강진장흥#1 T/L","장흥S/S 장기사용 GIS 대체공사","강진-장흥#1T/L GIS 대체 #2M.Tr 1차 GIS 대체","2020-10-19 09:00","2020-11-08 18:00","2020-11-02 09:00","2020-11-15 18:00","연속"]
[495,"광주전남","강진","강진장흥#2 T/L","장흥S/S 장기사용 GIS 대체공사","강진-장흥#1T/L GIS 대체관련 안전 이격거리 확보","2020-10-05 09:00","2020-10-18 18:00","2020-10-19 09:00","2020-11-01 18:00","매일"]
[496,"광주전남","강진","강진장흥#1 T/L","장흥S/S 장기사용 GIS 대체공사","강진-장흥#1T/L GIS 대체 #2M.Tr 1차 GIS 대체","2020-10-05 09:00","2020-10-08 18:00","2020-10-19 09:00","2020-10-22 18:00","매일"]
[497,"광주전남","강진","장흥벌교 T/L","장흥S/S 장기사용 GIS 대체공사","장흥S/S 154kV #2BUS 무부하 가압 장흥S/S 154kV #1BUS 무부하 가압","2020-10-19 18:00","2020-11-08 18:00","2020-11-02 09:00","2020-11-15 18:00","연속"]
[498,"광주전남","강진","장흥S/S 154kV #1 BUS","장흥S/S 장기사용 GIS 대체공사","강진-장흥#1T/L GIS 대체관련 모선 대체 #2M.Tr 1차 GIS 대체관련 모선 대체","2020-10-26 09:00","2020-11-08 18:00","취소","취소","연속"]
[499,"광주전남","강진","해남진도#2 T/L","2020 광주전남 관내 OPGW 항공장애표시구 설치공사","2020 광주전남 관내 OPGW 항공장애표시구 설치공사 (해남-진도 26~100)","2020-10-19 09:00","2020-10-20 18:00","2020-10-19 09:00","2020-10-20 18:00","매일"]
[500,"광주전남","광주","일곡비아#2 T/L","일곡S/S 154kV #4M.Tr 증설공사","일곡S/S 154kV #4M.Tr 증설공사 154kV #65BUS 설치","2020-10-19 09:00","2020-10-24 18:00","2020-10-05 09:00","2020-10-09 18:00","연속"]
[501,"광주전남","광주","신광주일곡#1 T/L","2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사 - 일곡S/S : GIS CB, 상부BUS 정밀점검 - 신광주S/S : LS산전제 DS Shaft축 마모관련 621DS 정밀점검","2020-10-21 09:00","2020-10-23 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[502,"광주전남","광주","신광주일곡#2 T/L","2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사","2020-10-19 09:00","2020-10-20 18:00","2020-10-28 09:00","2020-10-29 18:00","연속"]
[503,"광주전남","광주","하남장성#1 T/L","2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사","2020-11-09 09:00","2020-11-11 18:00","취소","취소","연속"]
[504,"광주전남","광주","신광주장성#1 T/L","2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사","2020-11-02 09:00","2020-11-04 18:00","취소","취소","연속"]
[505,"광주전남","광주","계림충장#3 T/L","2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[506,"광주전남","목포","나주엄다#1 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#1T/L 정밀점검 - 나주S/S ~ 엄다S/S, 116기","2020-10-05 08:00","2020-10-08 18:00","2020-10-05 08:00","2020-10-08 18:00","매일"]
[507,"광주전남","목포","나주엄다#2 T/L","2020년도 목포전력 가공송전선로 순시점검 위탁공사","○ 154kV 나주-엄다#2T/L 정밀점검 - 나주S/S ~ 엄다S/S, 116기","2020-10-12 08:00","2020-10-16 18:00","2020-10-12 08:00","2020-10-16 18:00","매일"]
[508,"광주전남","순천","광양하동#2 T/L","154kV 광양-하동#2 T/L 정밀점검","20년도 가공송전 순시점검 위탁공사 - 광양-하동#2 T/L 정밀점검 : No.38~91호(53기)","2020-10-22 08:00","2020-10-23 18:00","2020-10-14 08:00","2020-10-15 18:00","연속"]
[509,"광주전남","순천","광양하동#1 T/L","154kV 광양-하동#1 T/L 정밀점검","20년도 가공송전 순시점검 위탁공사 - 광양-하동#1 T/L 정밀점검 : No.38~91호(53기)","2020-10-20 08:00","2020-10-21 18:00","2020-10-12 08:00","2020-10-13 18:00","연속"]
[510,"광주전남","순천","서순천주암HP#1 T/L","20-21년 변전정비회사 총액공사","서순천SS 서순천-주암HPT/L GIS 타임측정","2020-10-30 09:00","2020-10-30 18:00","2020-10-30 09:00","2020-10-30 18:00","연속"]
[511,"광주전남","순천","여수소라#2 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여수,소라S/S 154kV 여수-소라#2T/L 보호반 대체","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","연속"]
[512,"광주전남","순천","여수소라#1 T/L","20-21년 순천전력지사 변전정비회사 총액공사","여수,소라S/S 154kV 여수-소라#1T/L 보호반 대체","2020-10-06 09:00","2020-10-08 18:00","2020-10-06 09:00","2020-10-08 18:00","연속"]
[513,"광주전남","순천","여수T/P 154kV SEC CB 60610","20-21년 순천전력지사 변전정비회사 총액공사","여수TP 154kV #60-65 모선보호반 대체","2020-10-26 09:00","2020-10-29 18:00","취소","취소","연속"]
[514,"광주전남","순천","여수T/P 154kV SEC CB 65660","20-21년 순천전력지사 변전정비회사 총액공사","여수TP 154kV #60-65 모선보호반 대체","2020-10-26 09:00","2020-10-29 18:00","취소","취소","연속"]
[515,"광주전남","순천","여수T/P 154kV CB 6100","20-21년 순천전력지사 변전정비회사 총액공사","여수TP 154kV #60-65 모선보호반 대체","2020-10-26 09:00","2020-10-29 18:00","취소","취소","연속"]
[516,"광주전남","순천","율촌화치#2 T/L","종합예방진단시스템 3차분 설치공사","화치S/S 율촌-화치#2T/L 차폐 및 센서 설치","2020-10-13 09:00","2020-10-13 18:00","2020-10-13 09:00","2020-10-13 18:00","연속"]
[517,"광주전남","순천","여수TP화치#1 T/L","154kV 여수TP화치 #1T/L 정밀점검","가공송전 순시점검 위탁공사","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","매일"]
[518,"광주전남","순천","율촌화치#1 T/L","종합예방진단시스템 3차분 설치공사","화치S/S 율촌-화치#1T/L 차폐 및 센서 설치","2020-10-12 09:00","2020-10-12 18:00","2020-10-12 09:00","2020-10-12 18:00","연속"]
[519,"광주전남","순천","여수TP화치#2 T/L","154kV 여수TP화치 #2T/L 정밀점검","가공송전 순시점검 위탁공사","2020-10-28 09:00","2020-10-29 18:00","2020-10-28 09:00","2020-10-29 18:00","매일"]
[520,"광주전남","직할","충장농성#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체","2020-09-07 09:00","2020-10-09 18:00","취소","취소","연속"]
[521,"광주전남","직할","남광주금천#1 T/L","2020~21년 직할 송전정비회사 총액공사","송전철탑 추락방지시설 설치공사 시행 - 154kV 남광주-금천T/L 77호","2020-10-26 08:00","2020-10-27 18:00","2020-10-26 08:00","2020-10-27 18:00","매일"]
[522,"광주전남","직할","나주금천#2 T/L","2020~21년 직할 송전정비회사 총액공사","송전철탑 추락방지시설 설치공사 관련 4회선 병가구간 안전이격거리 확보차 - 154kV 남광주-금천T/L 77호","2020-10-26 08:00","2020-10-27 18:00","2020-10-26 08:00","2020-10-27 18:00","매일"]
[523,"광주전남","직할","남광주금천#2 T/L","2020~21년 직할 송전정비회사 총액공사","송전철탑 추락방지시설 설치공사 시행 - 154kV 남광주-금천T/L 77호","2020-10-28 08:00","2020-10-29 18:00","2020-10-28 08:00","2020-10-29 18:00","매일"]
[524,"광주전남","직할","나주금천#1 T/L","2020~21년 직할 송전정비회사 총액공사","송전철탑 추락방지시설 설치공사 관련 4회선 병가구간 안전이격거리 확보차 - 154kV 남광주-금천T/L 77호","2020-10-28 08:00","2020-10-29 18:00","2020-10-28 08:00","2020-10-29 18:00","매일"]
[525,"광주전남","직할","농성화정#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체관련 무부하선로","2020-10-07 18:00","2020-10-08 09:00","2020-10-07 18:00","2020-10-08 09:00","연속"]
[526,"광주전남","직할","농성화정#1 T/L","농성E/C 154kV 이하 장기사용 GIS(Digital화) 교체 공사","충장-농성#1T/L, #1M.Tr 1차 GIS 교체관련 무부하선로","2020-10-08 18:00","2020-10-09 18:00","2020-10-08 18:00","2020-10-09 18:00","연속"]
[527,"광주전남","직할","왕곡나주#1 T/L","154kV 왕곡 실증시험장 건설공사","154kV 왕곡 실증시험장 무부하가압","2020-10-20 18:00","2020-10-21 18:00","2020-10-20 18:00","2020-10-21 18:00","연속"]
[528,"광주전남","직할","하남평동#1 T/L","154kV 덕림분기 T/L 건설공사","전력선 가선공사(하남평동T/L No.7~ 덕림분기T/L No.33호, 13.7km)","2020-09-01 09:00","2020-10-22 18:00","취소","취소","연속"]
[529,"광주전남","직할","하남평동#2 T/L","154kV 덕림분기 T/L 건설공사","전력선 가선공사(하남평동T/L No.7~ 덕림분기T/L No.33호, 13.7km)","2020-10-14 09:00","2020-11-08 18:00","2020-10-14 09:00","2020-11-08 18:00","연속"]
[530,"광주전남","직할","매월화정#1 T/L","2020년 직할 관내 170kV GIS 정밀점검 공사","ㅇ 매월-화정#1T/L 정밀점검","2020-10-15 09:00","2020-10-16 12:00","2020-10-15 09:00","2020-10-16 18:00","연속"]
[531,"광주전남","직할","매월화정#2 T/L","'19~20년 지중송전설비 위탁정비공사","- 19년 상반기 맨홀점검 시 발견된 절연통보호장치(SVL) 열화 및 절연파괴 개소 정비(교체)작업","2020-10-13 09:00","2020-10-14 18:00","2020-10-13 09:00","2020-10-14 18:00","연속"]
[532,"대구","경산","대구범물#1 T/L","경산P/O 하반기 정밀점검공사","- 657GIS 차단부 정밀점검 관련 무부하 가압선로","2020-10-20 17:00","2020-10-20 18:00","2020-10-20 17:00","2020-10-20 18:00","연속"]
[533,"대구","경산","범물S/S 154kV 고속철도대구#2 T/L CB","경산P/O 하반기 정밀점검공사","- 687 GIS 차단부 정밀점검 및 공기조작부(전자변) 교체","2020-10-22 09:00","2020-10-23 18:00","2020-10-22 09:00","2020-10-23 18:00","연속"]
[534,"대구","경산","안심대구그린파워#1 T/L","2020~21년 경산변전협력 총액공사","-장기미동작시험 및 선로정수측정","2020-10-19 09:00","2020-10-19 13:00","2020-10-19 09:00","2020-10-19 13:00","연속"]
[535,"대구","경산","안심반야월#2 T/L","경산P/O 하반기 정밀점검공사","- 627 GIS 공기조작부(전자변) 교체","2020-10-28 09:00","2020-10-28 18:00","2020-10-28 09:00","2020-10-28 18:00","연속"]
[536,"대구","경산","안심반야월#1 T/L","경산P/O 하반기 정밀점검공사","- 617GIS 차단부 정밀점검 및 공기조작부(전자변) 교체","2020-10-29 09:00","2020-10-30 18:00","2020-10-29 09:00","2020-10-30 18:00","연속"]
[537,"대구","경산","안심대구그린파워#2 T/L","2020~21년 경산변전협력 총액공사","-장기미동작시험 및 선로정수측정","2020-10-19 13:00","2020-10-19 18:00","2020-10-19 13:00","2020-10-19 18:00","연속"]
[538,"대구","경산","진량노변 T/L","20년 하반기 경산P/O 170kV GIS 정밀점검","- 진량 647GIS 정밀점검","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[539,"대구","경산","신경산진량 T/L","20년 하반기 경산P/O 170kV GIS 정밀점검","- 진량 6133GIS 정밀점검무부하가압선로","2020-10-08 17:00","2020-10-08 18:00","2020-10-08 17:00","2020-10-08 18:00","연속"]
[540,"대구","경산","신경산진량 T/L","20년 하반기 경산P/O 170kV GIS 정밀점검","- 진량 6333GIS 정밀점검무부하가압선로","2020-10-15 17:00","2020-10-15 18:00","2020-10-15 17:00","2020-10-15 18:00","연속"]
[541,"대구","경산","신경산진량 T/L","20년 하반기 경산P/O 170kV GIS 정밀점검","- 진량 6233GIS 정밀점검무부하가압선로","2020-10-13 17:00","2020-10-13 18:00","2020-10-13 17:00","2020-10-13 18:00","연속"]
[542,"대구","달성","고령S/S 154kV #65 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-18 18:00","2020-10-19 18:00","2020-10-18 18:00","2020-10-19 18:00","연속"]
[543,"대구","달성","고령S/S 154kV #66 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-18 17:00","2020-10-18 18:00","2020-10-18 17:00","2020-10-18 18:00","연속"]
[544,"대구","달성","고령다산#2 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-14 08:00","2020-10-19 18:00","2020-10-14 08:00","2020-10-19 18:00","연속"]
[545,"대구","달성","고령쌍림#2 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-14 08:00","2020-10-20 18:00","2020-10-14 08:00","2020-10-20 18:00","연속"]
[546,"대구","달성","고령S/S 154kV #61 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-24 17:00","2020-10-24 18:00","2020-10-24 17:00","2020-10-24 18:00","연속"]
[547,"대구","달성","고령쌍림#2 T/L","고령S/S #1Sh.C CB 정밀점검[Test용]","고령S/S #1Sh.C CB 정밀점검[Test용]","2020-10-06 13:00","2020-10-06 18:00","2020-10-06 13:00","2020-10-06 18:00","연속"]
[548,"대구","달성","고령S/S 154kV #60 BUS","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-24 18:00","2020-10-25 18:00","2020-10-24 18:00","2020-10-25 18:00","연속"]
[549,"대구","달성","고령쌍림#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-20 08:00","2020-10-24 18:00","2020-10-20 08:00","2020-10-24 18:00","연속"]
[550,"대구","달성","고령다산#1 T/L","고령S/S 154kV 송전선로 인출변경","고령S/S 154kV 송전선로 인출변경 및 보호반 대체","2020-10-20 08:00","2020-10-25 18:00","2020-10-20 08:00","2020-10-25 18:00","연속"]
[551,"대구","달성","고령쌍림#2 T/L","고령S/S #2Sh.C CB 정밀점검[Test용]","고령S/S #2Sh.C CB 정밀점검[Test용]","2020-10-08 13:00","2020-10-08 18:00","2020-10-08 13:00","2020-10-08 18:00","연속"]
[552,"대구","달성","논공달성#1 T/L","20-21년 가공송전정비회사 총액공사","애자련 교체(No.4)","2020-10-13 08:00","2020-10-13 14:00","2020-10-13 08:00","2020-10-13 14:00","연속"]
[553,"대구","달성","논공달성#2 T/L","20-21년 가공송전정비회사 총액공사","애자련 교체(No.4)","2020-10-13 14:00","2020-10-13 18:00","2020-10-13 14:00","2020-10-13 18:00","연속"]
[554,"대구","달성","논공현풍#2 T/L","지중송전 피뢰기 점검","154kV 논공-현풍#2T/L 지중인출 피뢰기 점검","2020-10-16 14:00","2020-10-16 18:00","2020-10-16 14:00","2020-10-16 18:00","연속"]
[555,"대구","달성","논공현풍#1 T/L","지중송전 피뢰기 점검","154kV 논공-현풍#1T/L 지중인출 피뢰기 점검","2020-10-16 09:00","2020-10-16 14:00","2020-10-16 09:00","2020-10-16 14:00","연속"]
[556,"대구","달성","두류봉덕#1 T/L","두류,봉덕S/S 두류-봉덕#1T/L 보호반 대체","두류,봉덕S/S 두류-봉덕#1T/L 보호반 대체","2020-10-22 09:00","2020-10-23 18:00","2020-10-22 09:00","2020-10-23 18:00","연속"]
[557,"대구","달성","두류봉덕#2 T/L","두류,봉덕S/S 두류-봉덕#2T/L 보호반 대체","두류,봉덕S/S 두류-봉덕#2T/L 보호반 대체","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[558,"대구","달성","상인봉덕#1 T/L","지중송전 피뢰기 점검","154kV 상인-봉덕#1T/L 지중인출 피뢰기 점검","2020-10-15 09:00","2020-10-15 14:00","2020-10-15 09:00","2020-10-15 14:00","연속"]
[559,"대구","달성","상인봉덕#2 T/L","지중송전 피뢰기 점검","154kV 상인-봉덕#2T/L 지중인출 피뢰기 점검","2020-10-15 14:00","2020-10-15 18:00","2020-10-15 14:00","2020-10-15 18:00","연속"]
[560,"대구","달성","현풍유가#1 T/L","유가S/S 154kV 현풍-유가#1T/L LA 초기점검","유가S/S 154kV 현풍-유가#1T/L LA 초기점검","2020-10-28 09:00","2020-10-28 14:00","2020-10-28 09:00","2020-10-28 14:00","연속"]
[561,"대구","달성","현풍유가#2 T/L","유가S/S 154kV 현풍-유가#2T/L LA 초기점검","유가S/S 154kV 현풍-유가#2T/L LA 초기점검","2020-10-28 14:00","2020-10-28 18:00","2020-10-28 14:00","2020-10-28 18:00","연속"]
[562,"대구","직할","공평침산 T/L","변전소 인출구간 OF 선종교체 공사","OF선종을 XLPE 선종으로 교체 구간 : 공평EBG J/B#4","2020-10-06 09:00","2020-11-11 18:00","2020-10-06 09:00","2020-11-11 18:00","연속"]
[563,"대구","직할","내당두류#2 T/L","내당-두류#2 보호반 교체작업","내당,두류S/S 내당-두류#2 보호반 교체작업","2020-10-19 09:30","2020-10-21 18:00","2020-10-19 09:30","2020-10-21 18:00","연속"]
[564,"대구","직할","내당두류#1 T/L","내당-두류#1 보호반 교체작업","내당,두류S/S 내당-두류#1 보호반 교체작업","2020-10-14 09:30","2020-10-16 18:00","2020-10-14 09:30","2020-10-16 18:00","연속"]
[565,"대구","포항","영일포항#2 T/L","154kV 영일-포항T/L 안전이격거리확보공사 (2회선 동시휴전)","-철탑 설치 1기 (신설 No.14) -철탑 보강 1기 (No.15) -철탑 철거 1기 (기설 No.14) -전선 교체 (No.13~15, HSTACIR/AW 410mm x S x 2C, 2.295C-km)","2020-10-26 08:00","2020-10-30 18:00","2020-10-26 08:00","2020-10-30 18:00","연속"]
[566,"대구","포항","영일포항#1 T/L","154kV 영일-포항T/L 안전이격거리확보공사 (2회선 동시휴전)","-철탑 설치 1기 (신설 No.14) -철탑 보강 1기 (No.15) -철탑 철거 1기 (기설 No.14) -전선 교체 (No.13~15, HSTACIR/AW 410mm x S x 2C, 2.295C-km)","2020-10-26 08:00","2020-10-30 18:00","2020-10-26 08:00","2020-10-30 18:00","연속"]
[567,"경북","구미","남인동S/S 154kV CB 6100","남인동S/S 170kV GIS교체공사[2차수]","- 남인동-인동#2T/L(677), BUS-TIE(6100), PT+ES GIS교체","2020-10-07 09:00","2020-10-30 18:00","2020-10-07 09:00","2020-10-30 18:00","연속"]
[568,"경북","구미","남인동S/S 154kV #1 BUS","남인동S/S 170kV GIS교체공사[2차수]","- 남인동-인동#2T/L(677), BUS-TIE(6100), PT+ES GIS교체","2020-10-08 09:00","2020-10-20 09:00","2020-10-08 09:00","2020-10-20 09:00","연속"]
[569,"경북","구미","남인동인동#2 T/L","남인동S/S 170kV GIS교체공사[2차수]","- 남인동-인동#2T/L(677), BUS-TIE(6100), PT+ES GIS교체","2020-10-07 09:00","2020-10-30 18:00","2020-10-07 09:00","2020-10-30 18:00","연속"]
[570,"경북","영주","점촌문경 T/L","2020~21년도 영주전력지사 변전정비회사 총액공사","- 점촌S/S 657 차단기 보통점검 및 전자변 교체, PT 보통점검 - 문경S/S 617 차단기 보통점검, LA 보통점검","2020-10-17 09:00","2020-10-17 18:00","2020-10-17 09:00","2020-10-17 18:00","연속"]
[571,"경북","직할","안동C/C 154kV CB 6100","20~21년 경북본부 직할 변전정비회사 총액공사","안동복합S/S 154kV BUS-TIE GIS 조작시험","2020-10-20 15:00","2020-10-20 18:00","2020-10-20 15:00","2020-10-20 18:00","연속"]
[572,"경북","직할","안동풍산 T/L","154kV 안동-풍산 등 2개T/L 지장선로 임시이설공사","○ 공사구간 : 154kV 안동-풍산T/L No.59~64 ○ 지지물 설치 3기, 철거 4기 ○ 전력선 HSTACIR/AW 240㎟ × S, ACSR 410㎟ × S, 0.971km","2020-10-22 07:00","2020-10-27 18:00","취소","취소","연속"]
[573,"경북","직할","울진현종산풍력 T/L","'20-21년 경북직할 가공송전 정비회사 총액공사","ㅇ154kV울진-현종산풍력T/L No.79 철탑상부재보강","2020-10-21 08:00","2020-10-23 18:00","2020-10-21 08:00","2020-10-23 18:00","매일"]
[574,"강원","강릉","속초간성#2 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 불량애자교체 : 154kV 간성 #2T/L No.42","2020-10-20 08:00","2020-10-20 18:00","취소","취소","연속"]
[575,"강원","강릉","강릉횡계#2 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-14 10:00","2020-10-14 18:00","취소","취소","연속"]
[576,"강원","강릉","강릉횡계#1 T/L","2020년 170kV GIS 하자점검","○ 2020년 170kV GIS 하자점검 : 강릉S/S 강릉-횡계#1T/L ○ 2020년 장기미동작 차단기 조작시험 : 횡계S/S 강릉횡계#1T/L","2020-10-19 10:00","2020-10-19 18:00","취소","취소","연속"]
[577,"강원","강릉","강릉횡계#1 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 불량애자교체 : 154kV 강릉횡계#1T/L No.33","2020-10-26 08:00","2020-10-26 18:00","취소","취소","연속"]
[578,"강원","강릉","동해강릉 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ 154kV 강릉-횡계#1T/L 불량애자교체작업 4회선구간 휴전","2020-10-26 08:00","2020-10-26 18:00","취소","취소","연속"]
[579,"강원","강릉","신양양양양#1 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-12 10:00","2020-10-12 18:00","취소","취소","연속"]
[580,"강원","강릉","동해영동TP T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○SB댐퍼, 스페이서, 노후금구류 교체 : 154kV 동해분기T/L No.1~53(34기), 154kV 강릉T/L No.1~8(8기)","2020-10-05 08:00","2020-10-15 18:00","취소","취소","매일"]
[581,"강원","강릉","신제천주진#1 T/L","2020~2021년도 원주전력지사 송전정비회사 총액공사","○ 전선 접속개소 해소공사","2020-10-26 07:00","2020-10-29 18:00","취소","취소","연속"]
[582,"강원","강릉","신제천주진#2 T/L","2020~2021년도 원주전력지사 송전정비회사 총액공사","○ 전선 접속개소 해소공사","2020-10-30 07:00","2020-11-02 18:00","취소","취소","연속"]
[583,"강원","강릉","주진평창#2 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ SB댐퍼 교체 및 신설 : 154kV 주진평창 #2T/L No.2~ST(23기)","2020-10-27 08:00","2020-10-30 18:00","취소","취소","매일"]
[584,"강원","강릉","주진평창#1 T/L","20-21년도 강릉전력지사 송전정비회사 총액공사","○ SB댐퍼, 불량애자교체 : 154kV 주진평창T/L No.2~ST(23기)","2020-10-21 08:00","2020-10-26 18:00","취소","취소","매일"]
[585,"강원","강릉","횡계올림픽 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-16 10:00","2020-10-16 18:00","취소","취소","연속"]
[586,"강원","강릉","횡계평창 T/L","2020년 장기미동작 차단기 조작시험","○ 2020년 장기미동작 차단기 조작시험","2020-10-15 10:00","2020-10-15 18:00","취소","취소","연속"]
[587,"강원","동해","동해동영월 T/L","154kV 영월화력T/L No.124 안전이격확보공사","안전이격확보공사","2020-10-19 08:00","2020-10-23 18:00","취소","취소","연속"]
[588,"강원","동해","동해T/P 154kV #2 BUS","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-10-13 09:00","2020-10-20 18:00","취소","취소","연속"]
[589,"강원","동해","삼척동해TP T/L","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-09-24 09:00","2020-10-23 18:00","취소","취소","연속"]
[590,"강원","동해","동해T/P 154kV #1 BUS","동해화력S/Y 장기사용 170kV GIS 대체공사","- 동해화력S/Y 장기사용 170kV GIS 6CCT대체 - 동해화력S/Y 부분디지털화 공사","2020-10-05 09:00","2020-10-12 18:00","취소","취소","연속"]
[591,"강원","동해","삼척G/P 154kV SEC CB 61620","삼척GP 170kV GIS 스페이서 교체공사","1. 가스 누기부 스페이서 교체","2020-10-19 09:00","2020-10-23 18:00","취소","취소","연속"]
[592,"강원","동해","정선영월CC T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48)31.688kM 교체 - 항공장애표시구 71개 철거 및 설치","2020-10-21 08:00","2020-11-14 18:00","취소","취소","연속"]
[593,"강원","원주","남원주원주#1 T/L","2020년 원주전력지사 변전정비회사 총액공사","임시 SPS 계전기 및 제어케이블 철거","2020-10-21 09:00","2020-10-21 18:00","취소","취소","연속"]
[594,"강원","원주","원주서원주#1 T/L","세니온제 보호배전반 성능개선","- 보호계전기 성능개선 시행","2020-10-14 10:30","2020-10-14 18:00","취소","취소","연속"]
[595,"강원","원주","홍천상남#2 T/L","2020년 원주전력지사 변전정비회사 총액공사","상시여자형 보조Ry 과열 및 이음발생 교체 - K102, VX 게전기","2020-10-22 09:00","2020-10-22 18:00","취소","취소","연속"]
[596,"강원","원주","횡성홍천#1 T/L","154kV 홍천T/L No.60~67 안전이격 확보공사","○ 철탑교체 : 4기(No.60,61,62,63)","2020-10-12 07:00","2020-10-21 18:00","취소","취소","연속"]
[597,"강원","원주","홍천소양강HP T/L","2020~2021년 강원직할 송전정비회사 총액공사","안전이격확보공사(철탑교체 및 전력선 교체)","2020-10-20 07:00","2020-10-23 18:00","취소","취소","연속"]
[598,"강원","원주","횡성홍천#1 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV GIS 월부싱교체 안전이격확보","2020-10-07 08:00","2020-10-07 18:00","취소","취소","연속"]
[599,"강원","원주","횡성홍천#2 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV 장기사용 GIS 철거/설치 ㅇ 디지털화공사 케이블 철거 및 광케이블 포설 ㅇ SA 운영장치 시험","2020-10-05 10:00","2020-10-30 18:00","취소","취소","연속"]
[600,"강원","원주","횡성홍천#1 T/L","횡성S/S 170kV GIS 장기사용 GIS 대체공사","ㅇ 170kV GIS 월부싱교체 안전이격확보","2020-10-16 08:00","2020-10-17 18:00","취소","취소","매일"]
[601,"강원","직할","남춘천춘천열병합#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량애자 교체","2020-10-08 09:00","2020-10-08 18:00","취소","취소","연속"]
[602,"강원","직할","남춘천춘천열병합#1 T/L","2020년 하반기 강원 직할 154kV GIS 정밀점검","154kV GIS 정밀점검","2020-10-26 09:00","2020-10-28 18:00","취소","취소","연속"]
[603,"강원","직할","홍천남춘천 T/L","2020년 하반기 장기 미동작 차단기 조작시험","남춘천S/S 154kV 홍천-남춘천 T/L 차단기 조작시험","2020-10-29 10:00","2020-10-29 14:00","취소","취소","연속"]
[604,"강원","직할","남춘천춘천 T/L","2020~2021년 강원직할 송전정비회사 총액공사","안전이격확보공사(철탑교체 및 전력선 교체)","2020-10-16 07:00","2020-10-19 18:00","취소","취소","연속"]
[605,"강원","직할","북춘천화천HP T/L","2020년 하반기 장기 미동작 차단기 조작시험","북춘천S/S 154kV 북춘천-화천HP T/L 차단기 조작시험","2020-10-29 14:00","2020-10-29 18:00","취소","취소","연속"]
[606,"강원","직할","서홍천춘천열병합 T/L","2020년 하반기 장기 미동작 차단기 조작시험","서홍천S/S 154kV 서홍천-춘천열병합 T/L 차단기 조작시험","2020-10-30 10:00","2020-10-30 18:00","취소","취소","연속"]
[607,"강원","직할","양구화천HP#1 T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량개소 정비(B-C링크 철거)","2020-10-12 08:00","2020-10-12 13:00","취소","취소","연속"]
[608,"강원","직할","상남인제#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","섬락애자 교체 No.91 등 4기","2020-10-06 07:00","2020-10-06 18:00","취소","취소","연속"]
[609,"강원","직할","춘천소양강HP T/L","2020~2021년 강원직할 송전정비회사 총액공사","불량애자교체","2020-10-15 07:00","2020-10-15 18:00","취소","취소","연속"]
[610,"강원","직할","춘천북춘천#2 T/L","2020~2021년 강원직할 송전정비회사 총액공사","와이어형 추락방지시설설치 및 B-C링크 철거","2020-10-14 07:00","2020-10-14 18:00","취소","취소","연속"]
[611,"강원","직할","춘천북춘천#1 T/L","2020~2021년 강원직할 송전정비회사 총액공사","와이어형 추락방지시설설치 및 B-C링크 철거","2020-10-13 07:00","2020-10-13 18:00","취소","취소","연속"]
[612,"강원","직할","춘천H/P 154kV CB 6233","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[613,"강원","직할","춘천H/P 154kV CB 6133","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[614,"강원","직할","춘천H/P 154kV #60 BUS","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[615,"강원","직할","청평PP춘천열병합 T/L","2020년 하반기 장기 미동작 차단기 조작시험","춘천열병합S/Y 154kV 청평PP-춘천열병합T/L 차단기 조작시험","2020-10-07 14:00","2020-10-07 18:00","취소","취소","연속"]
[616,"강원","직할","춘천열병합 154kV CB 6283","2020년 하반기 장기 미동작 차단기 조작시험","춘천열병합S/Y Stataion Aux Tr 1차 차단기 조작시험","2020-10-07 10:00","2020-10-07 14:00","취소","취소","연속"]
[617,"강원","직할","철원화천#1 T/L","화천S/S 드라이비트 보수공사","외벽드라이비트 탈락 및 파손 보수","2020-10-06 09:00","2020-10-06 18:00","취소","취소","연속"]
[618,"강원","직할","철원화천#2 T/L","화천S/S 드라이비트 보수공사","외벽드라이비트 탈락 및 파손 보수","2020-10-06 09:00","2020-10-06 18:00","취소","취소","연속"]
[619,"강원","직할","화천화천HP#2 T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","화천S/S 154kV 화천-화천HP #2 T/L 차단기 조작시험, LA 보통점검","2020-10-07 10:00","2020-10-08 18:00","취소","취소","매일"]
[620,"강원","직할","화천H/P 154kV #1 BUS","20~21 강원본부 직할 변전정비 총액공사","#4M.Tr 2차 DS 보통점검","2020-10-29 09:00","2020-10-29 14:00","취소","취소","연속"]
[621,"강원","직할","화천H/P 154kV #2 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #2 DS 보통점검 ○ #2 BUS CVT 보통점검","2020-10-07 14:00","2020-10-07 18:00","취소","취소","연속"]
[622,"강원","직할","화천H/P 154kV CB 6433","2020년 하반기 강원 직할 154kV GIS 정밀점검","154kV CB 정밀점검","2020-10-29 09:00","2020-10-31 18:00","취소","취소","연속"]
[623,"강원","직할","화천H/P 154kV #2 BUS","20~21 강원본부 직할 변전정비 총액공사","#4M.Tr 2차 DS 보통점검","2020-10-29 14:00","2020-10-29 18:00","취소","취소","연속"]
[624,"강원","직할","화천화천HP#1 T/L","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1, 2 DS 보통점검","2020-10-07 10:00","2020-10-07 18:00","취소","취소","연속"]
[625,"강원","직할","양구화천HP#2 T/L","2020년 하반기 장기 미동작 차단기 조작시험","화천HP 154kV 양구-화천H/P #2 T/L 차단기 조작시험","2020-10-05 10:00","2020-10-05 18:00","취소","취소","연속"]
[626,"강원","직할","화천H/P 154kV #1 BUS","20~21 강원본부 직할 변전정비 총액공사","○ 화천-화천H/P #1T/L #1 DS 보통점검 ○ #1 BUS CVT 보통점검","2020-10-07 10:00","2020-10-07 14:00","취소","취소","연속"]
[627,"강원","태백","신제천영월CC#2 T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48) 0.735km 교체","2020-10-07 08:00","2020-10-08 18:00","취소","취소","연속"]
[628,"강원","태백","동영월영월CC T/L","영월-동영월-정선간 OPGW 교체공사","- OPGW(OP-S-L48) 14.46km 교체 - 학공장애표시구 50개 철거 및 설치","2020-10-07 08:00","2020-10-17 18:00","취소","취소","연속"]
[629,"강원","태백","태백삼척GP#1 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거","2020-10-18 08:00","2020-10-25 18:00","취소","취소","연속"]
[630,"강원","태백","태백삼척GP#2 T/L","154kV 울진T/L 안전이격확보공사","전선 설치 및 철거(※ 태백-삼척GP #2 T/L 의 경우 10.11(일) 당일 No.80에서 점퍼분리 후 복구시행)","2020-10-18 08:00","2020-10-25 18:00","취소","취소","연속"]
[631,"강원","원주","신제천남원주#2 T/L","2020~2021년 원주전력지사 송전정비회사 총액공사","○ 성능저하 국산애자 교체(No.38,39,45)","2020-10-08 07:00","2020-10-08 18:00","취소","취소","연속"]
[632,"강원","직할","가평춘천HP T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[633,"강원","직할","북춘천춘천HP T/L","2020년~2021년 강원지역본부 직할 변전정비 총액공사","춘천H/P 154kV BUS PT 보통점검, 154kV 북춘천-춘천HP T/L BUS DS 보통점검, 154kV 가평-춘천HP T/L BUS DS 보통점검","2020-10-14 09:00","2020-10-14 18:00","취소","취소","연속"]
[634,"강원","원주","신제천남원주#1 T/L","2020~2021년 원주전력지사 송전정비회사 총액공사","○ 성능저하 국산애자 교체(No.38,39,45)","2020-10-07 07:00","2020-10-07 18:00","취소","취소","연속"]
[635,"부산울산","울산","울산울산TP#1 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산-울산TP#1T/L 보호반 43PD 수동 오류 조치(유호전기) - 울산T/P 154kV (신)울산-울산TP#2T/L GIS(627) #60BUS 시험가압 선로(24H이상)","2020-10-14 13:00","2020-10-15 18:00","2020-10-14 13:00","2020-10-15 18:00","연속"]
[636,"부산울산","울산","울주외동#2 T/L","철탑 추락방지시설 시범설치공사","추락방지장치 와이어형(수직,수평) 시범설치공사 - 구간 : 154kV 울주-외동T/L No.7,9","2020-10-19 09:00","2020-10-19 18:00","2020-10-30 07:00","2020-10-30 18:00","연속"]
[637,"부산울산","울산","울주외동#1 T/L","철탑 추락방지시설 시범설치공사","추락방지장치 와이어형(수직,수평) 시범설치공사 - 구간 : 154kV 울주-외동T/L No.7,9","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 07:00","2020-10-16 18:00","연속"]
[638,"부산울산","울산","웅촌서창#1 T/L","2020-21년 울산전력지사 변전협력회사 총액공사","-송전선로 보호반 대체","2020-10-12 09:00","2020-10-14 18:00","2020-10-12 09:00","2020-10-14 18:00","연속"]
[639,"부산울산","울산","용연처용#1 T/L","345kV 남울산S/S 건설공사","154kV 남울산-용연T/L 계통변경","2020-10-20 09:00","2020-10-25 18:00","2020-10-19 09:00","2020-10-25 18:00","연속"]
[640,"부산울산","직할","우동대연 T/L","20-21년 직할 변전정비회사 총액공사","대연S/S 우동-대연T/L GIS 보통점검","2020-10-24 09:30","2020-10-25 18:00","취소","취소","연속"]
[641,"부산울산","직할","범천S/S 154kV CB 6100","범천S/S 154kV 장기사용 GIS 대체공사(3차공정)","1.170kV 50kA 2,000A GIS(T/L) × 4CCT 대체 2.170kV 50kA 1,250A GIS(T/R) × 2CCT 대체 3.170kV 50kA 2,000A GIS(B/T) × 1CCT 대체 4.170kV 50kA PT&ES × 1CCT 대체 5.기타 부대공사 × 1식","2020-10-05 07:30","2020-10-16 18:00","2020-10-05 07:30","2020-10-16 18:00","연속"]
[642,"경남","직할","녹공마천#2 T/L","`20~21년도 경남본부 직할 송전정비회사 총액공사","ㅇ 지중선로용 피뢰기 교체 공사 시행 -154kV 녹공-마천#2T/L 녹공C/H(3EA), 마천C/H(3EA)","2020-10-30 08:00","2020-10-30 18:00","2020-10-30 08:00","2020-10-30 18:00","연속"]
[643,"경남","직할","녹공마천#1 T/L","`20~21년도 경남본부 직할 송전정비회사 총액공사","ㅇ 지중선로용 피뢰기 교체 공사 시행 -154kV 녹공-마천#1T/L 녹공C/H(3EA), 마천C/H(3EA)","2020-10-29 08:00","2020-10-29 18:00","2020-10-29 08:00","2020-10-29 18:00","연속"]
[644,"경남","직할","신김해장유#2 T/L","신김해S/S 154kV 장기사용GIS 교체공사(3차)","신김해S/S 154kV 장기사용GIS 교체공사(3차) 대상 : 신김해-장유#2T/L, #2BUS TIE, #2BUS PT, ES","2020-10-28 08:00","2020-11-17 18:00","2020-10-28 08:00","2020-11-17 18:00","연속"]
[645,"경남","직할","신김해진영#2 T/L","신김해- 창원#2 T/L 송전선로 정밀점검 안전확보","신김해-창원#2 송전선로 정밀점검(53) 안전확보","2020-10-05 08:00","2020-10-05 17:00","2020-10-05 08:00","2020-10-05 17:00","연속"]
[646,"경남","직할","신김해주촌#2 T/L","신김해S/S 154kV 장기사용GIS 교체공사(2차)","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-07 08:00","2020-10-27 18:00","2020-10-07 08:00","2020-10-27 18:00","연속"]
[647,"경남","직할","신김해지사#2 T/L","신김해S/S 154kV 장기사용GIS 교체공사(2차) - 안전이격","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-17 08:00","2020-10-17 18:00","2020-10-17 08:00","2020-10-17 18:00","연속"]
[648,"경남","직할","신김해지사#1 T/L","신김해S/S 154kV 장기사용GIS 교체공사(2차)","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-07 08:00","2020-10-27 18:00","2020-10-07 08:00","2020-10-27 18:00","연속"]
[649,"경남","직할","신김해S/S 154kV CB 6200","신김해S/S 154kV 장기사용GIS 교체공사(3차)","신김해S/S 154kV 장기사용GIS 교체공사(3차) 대상 : 신김해-장유#2T/L, #2BUS TIE, #2BUS PT, ES","2020-10-28 08:00","2020-11-17 18:00","2020-10-28 08:00","2020-11-17 18:00","연속"]
[650,"경남","직할","신김해지사#2 T/L","신김해S/S 154kV 장기사용GIS 교체공사(2차) - 안전이격","신김해S/S 154kV 장기사용GIS 교체공사(2차) 대상 : 신김해-지사#1, 주촌#2T/L","2020-10-24 08:00","2020-10-24 18:00","2020-10-24 08:00","2020-10-24 18:00","연속"]
[651,"경남","직할","신김해진영#1 T/L","신김해- 창원#1 T/L 송전선로 정밀점검 안전확보","신김해-창원#1 송전선로 정밀점검(53) 안전확보","2020-10-06 08:00","2020-10-06 17:00","취소","취소","연속"]
[652,"경남","직할","신월동읍#1 T/L","신월S/S 154kV #3M.Tr 1차 GIS 정밀점검(시험가압용)","신월S/S 154kV #3M.Tr 1차 GIS 정밀점검(시험가압용)","2020-10-30 16:00","2020-10-30 18:00","2020-10-30 16:00","2020-10-30 18:00","연속"]
[653,"경남","직할","신월동읍#2 T/L","신월S/S 154kV #3M.Tr 1차 GIS 정밀점검(시험가압용)","신월S/S 154kV #3M.Tr 1차 GIS 정밀점검(시험가압용)","2020-10-28 16:00","2020-10-28 18:00","2020-10-28 16:00","2020-10-28 18:00","연속"]
[654,"경남","직할","창원S/S 154kV #3 Sh.C CB","창원S/S 154kV Sh.C 설치공사","1. 154kV Sh.C × 2Bank 설치 2. 154kV GIS × 1CCT 이설 및 154kV GCB × 4대 설치 3. 154kV 전력케이블 포설·접속 및 종단접속함 설치 × 1식 4. 제어케이블 포설 및 기기기초 시공 × 1식 5. 기타 부대작업 × 1식","2020-10-26 09:00","2020-11-18 18:00","취소","취소","연속"]
[655,"경남","직할","창원S/S 154kV #4 Sh.C CB","창원S/S 154kV Sh.C 설치공사","1. 154kV Sh.C × 2Bank 설치 2. 154kV GIS × 1CCT 이설 및 154kV GCB × 4대 설치 3. 154kV 전력케이블 포설·접속 및 종단접속함 설치 × 1식 4. 제어케이블 포설 및 기기기초 시공 × 1식 5. 기타 부대작업 × 1식","2020-10-26 09:00","2020-11-18 18:00","취소","취소","연속"]
[656,"경남","진주","하동개양#2 T/L","154kV 하동-개양#1,2T/L 송전선로 정밀점검","154kV 하동-개양#1,2T/L 송전선로 정밀점검","2020-10-10 08:30","2020-10-11 17:00","2020-10-10 08:30","2020-10-11 17:00","매일"]
[657,"경남","진주","하동개양#1 T/L","154kV 하동-개양#1,2T/L 송전선로 정밀점검","154kV 하동-개양#1,2T/L 송전선로 정밀점검","2020-10-10 08:30","2020-10-11 17:00","2020-10-10 08:30","2020-10-11 17:00","매일"]
[658,"경남","진주","동진주S/S 154kV CB 6100","동진주S/S 154kV #1BUS TIE GIS 보통점검","동진주S/S 154kV #1BUS TIE GIS 보통점검","2020-10-06 10:00","2020-10-06 14:00","2020-10-06 10:00","2020-10-06 14:00","연속"]
[659,"경남","진주","함양거창#2 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 - 함양-거창#2T/L 이설 1. 함양-거창#2T/L C/H 연결 2. 함양-거창#2T/L 거창측 보호배전반 교체","취소","취소","취소","취소","연속"]
[660,"경남","통영","통영거제#2 T/L","154kV 통영-거제#2T/L 지중송전선로용 피뢰기 점검","154kV 통영-거제#2T/L 지중송전선로용 피뢰기 점검","2020-10-15 09:30","2020-10-15 17:00","2020-10-15 09:30","2020-10-15 17:00","연속"]
[661,"경남","통영","통영거제#1 T/L","154kV 통영-거제#1T/L 지중송전선로용 피뢰기 점검","154kV 통영-거제#1T/L 지중송전선로용 피뢰기 점검","2020-10-14 09:30","2020-10-14 17:00","2020-10-14 09:30","2020-10-14 17:00","연속"]
[662,"경남","통영","고성통영 T/L","154kV 고성-통영T/L 추락방지시설 설치","154kV 고성-통영T/L 추락방지시설 설치(146, 149호)","2020-10-18 08:00","2020-10-18 18:00","취소","취소","연속"]
[663,"경남","통영","신고성삼천포#1 T/L","삼천포S/S 170kV GIS 대체공사 3차공정 안전이격거리 확보","삼천포S/S 170kV GIS 대체공사 3차공정 - #2M.Tr 1차 GIS 대체 - 삼천포-사천#2T/L GIS 대체","2020-10-30 09:00","2020-11-02 18:00","2020-10-30 09:00","2020-11-02 18:00","연속"]
[664,"경남","통영","신고성삼천포#1 T/L","삼천포S/S 170kV GIS 대체공사 2차공정 시험가압선로","삼천포S/S 170kV GIS 대체공사 2차공정 - (구)B/T, PT&ES 철거 및 기능 이설 - #1M.Tr 1차 GIS 대체 - 삼천포-사천#1T/L GIS 대체","2020-10-18 13:00","2020-10-19 09:00","2020-10-19 18:00","2020-10-20 15:00","연속"]
[665,"경남","통영","신고성삼천포#2 T/L","삼천포S/S 170kV GIS 대체공사 2차공정 시험가압","삼천포S/S 170kV GIS 대체공사 2차공정 - (구)B/T, PT&ES 철거 및 기능 이설 - #1M.Tr 1차 GIS 대체 - 삼천포-사천#1T/L GIS 대체","2020-10-25 13:00","2020-10-26 09:00","2020-10-23 18:00","2020-10-24 18:00","연속"]
[666,"경남","통영","삼천포사천#2 T/L","삼천포S/S 170kV GIS 대체공사 3차공정","삼천포S/S 170kV GIS 대체공사 3차공정 - #2M.Tr 1차 GIS 대체 - 삼천포-사천#2T/L GIS 대체","2020-10-26 09:00","2020-11-14 18:00","2020-10-26 09:00","2020-11-14 18:00","연속"]
[667,"경남","통영","삼천포S/S 154kV #1 BUS","삼천포S/S 170kV GIS 대체공사 3차공정","삼천포S/S 170kV GIS 대체공사 3차공정 - #2M.Tr 1차 GIS 대체 - 삼천포-사천#2T/L GIS 대체","2020-10-27 16:00","2020-11-05 09:00","2020-10-27 16:00","2020-11-05 09:00","연속"]
[668,"경남","통영","삼천포사천#1 T/L","삼천포S/S 170kV GIS 대체공사 2차공정","삼천포S/S 170kV GIS 대체공사 2차공정 - (구)B/T, PT&ES 철거 및 기능 이설 - #1M.Tr 1차 GIS 대체 - 삼천포-사천#1T/L GIS 대체","2020-10-05 09:00","2020-10-26 09:00","2020-10-05 09:00","2020-10-26 09:00","연속"]
[669,"경남","통영","신고성삼천포#1 T/L","154kV 삼천포-사천#1T/L 불량애자 교체 안전이격확보","154kV 삼천포-사천#1T/L 불량애자 교체관련 안전이격확보","2020-10-05 08:00","2020-10-09 18:00","2020-10-05 08:00","2020-10-09 18:00","매일"]
[670,"경남","통영","신고성거제#1 T/L","154kV 신고성-거제#1T/L SB댐퍼 교체","154kV 신고성-거제#1T/L SB댐퍼 교체(145~146, 154~156호)","2020-10-10 08:00","2020-10-11 18:00","취소","취소","매일"]
[671,"경남","통영","신고성삼천포#2 T/L","154kV 삼천포-사천#2T/L 불량애자 교체 안전이격확보","154kV 삼천포-사천#2T/L 불량애자 교체관련 안전이격확보","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-29 18:00","매일"]
[672,"경남","통영","신고성통영 T/L","154kV 신고성-통영T/L 추락방지시설 설치","154kV 신고성-통영T/L 추락방지시설 설치(146, 149호)","2020-10-17 08:00","2020-10-17 18:00","취소","취소","연속"]
[673,"경남","함안","청도밀양#2 T/L","밀양변전소 외벽패널 설치 및 기타공사","○ 2층 170kV GIS실 상부 창호교체 (내부작업) - 휴전 전 : GIS실 내부 외벽면(부싱) 비계설치 - 휴전 후 : 상부 창호 교체 및 코킹작업","2020-10-20 09:00","2020-10-23 18:00","2020-10-20 09:00","2020-10-23 18:00","매일"]
[674,"경남","함안","청도밀양#1 T/L","밀양변전소 외벽패널 설치 및 기타공사","○ 2층 170kV GIS실 상부 창호교체 (내부작업) - 휴전 전 : GIS실 내부 외벽면(부싱) 비계설치 - 휴전 후 : 상부 창호 교체 및 코킹작업","2020-10-26 09:00","2020-10-30 18:00","2020-10-26 09:00","2020-10-30 18:00","매일"]
[675,"경남","함안","진영한림정#1 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 345k신김해-북부산T/L 95-96호 횡단구간 안전확보","2020-10-10 07:00","2020-10-11 18:00","2020-10-10 07:00","2020-10-11 18:00","연속"]
[676,"경남","함안","진영한림정#2 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 345k신김해-북부산T/L 95-96호 횡단구간 안전확보","2020-10-10 07:00","2020-10-11 18:00","2020-10-10 07:00","2020-10-11 18:00","연속"]
[677,"경남","함안","진영한림정#1 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 345k신김해-북부산T/L 95-96호 횡단구간 안전확보","2020-10-17 07:00","2020-10-18 18:00","2020-10-17 07:00","2020-10-18 18:00","연속"]
[678,"경남","함안","진영한림정#2 T/L","345kV 신김해-북부산T/L 94호 안전이격 확보공사","○ 345k신김해-북부산T/L 95-96호 횡단구간 안전확보","2020-10-17 07:00","2020-10-18 18:00","2020-10-17 07:00","2020-10-18 18:00","연속"]
[679,"경남","함안","신마산칠서#2 T/L","칠서S/S 154kV 장기사용 GIS 대체공사","칠서S/S 154kV 장기사용 GIS 대체공사","2020-10-27 18:00","2020-10-28 09:00","2020-10-27 18:00","2020-10-28 09:00","연속"]
[680,"경남","함안","칠서창녕#2 T/L","칠서S/S 154kV 장기사용 GIS 대체공사","칠서S/S 154kV 장기사용 GIS 대체공사","2020-10-26 09:00","2020-11-12 17:00","2020-10-26 09:00","2020-11-12 17:00","연속"]
[681,"경남","진주","함양거창#2 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 공사 1. 함양-거창#2T/L 휴전 2. 함양-거창#2T/L 가철탑으로 임시이설","2020-10-19 07:30","2020-10-19 19:00","2020-10-19 07:30","2020-10-19 19:00","연속"]
[682,"경남","진주","함양거창#1 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 공사 - (신)변전소 가압시행 1. 함양-거창#1T/L 휴전 2. 함양-거창#1T/L 보호계전기 이설작업 3. 함양S/S (신)변전소 시험가압 시행","2020-10-20 07:30","2020-10-23 19:00","2020-10-20 07:30","2020-10-23 19:00","연속"]
[683,"경남","진주","산청함양 T/L","함양S/S 옥외철구 현대화 공사","함양S/S 옥외철구 현대화 공사 - (신)함양으로 이설 1. 산청함양T/L 휴전 2. 산청함양T/L 보호계전기 이설작업 3. 산청함양T/L 인출변경","2020-10-24 08:00","2020-10-25 19:00","2020-10-24 08:00","2020-10-25 19:00","연속"]
[684,"부산울산","동부산","신양산구서#1 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 154kV 구서-명장#1T/L 안전이격확보용","2020-10-05 08:00","2020-10-06 18:00","2020-10-05 08:00","2020-10-06 18:00","연속"]
[685,"부산울산","동부산","구서명장#2 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 구서-명장#1 T/L 조류착지 방지장치 설치 ○ 대상 : 조류착지 방지장치-17개소","2020-10-15 08:00","2020-10-16 18:00","2020-10-15 08:00","2020-10-16 18:00","연속"]
[686,"부산울산","동부산","구서명장#1 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 압축인류크램프 정비 : 3, 20호 10개소","2020-10-05 08:00","2020-10-06 18:00","2020-10-05 08:00","2020-10-06 18:00","연속"]
[687,"부산울산","동부산","신양산구서#2 T/L","동부산전력지사 가공송전 취약설비 정비공사","ㅇ 압축인류크램프 정비 : 신양산S/T, 6~8, 19~22, 31, 34, 41호 18개소","2020-10-12 08:00","2020-10-16 18:00","2020-10-12 08:00","2020-10-16 18:00","연속"]
[688,"부산울산","동부산","구서명장#2 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 신양산-구서#2 T/L 안전이격확보용","2020-10-14 08:00","2020-10-14 18:00","2020-10-14 08:00","2020-10-14 18:00","연속"]
[689,"부산울산","동부산","신양산구서#1 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 신양산-구서#1 T/L 애자교체 공사 ○ 21,36,40호","2020-10-07 08:00","2020-10-08 18:00","2020-10-07 08:00","2020-10-08 18:00","연속"]
[690,"부산울산","동부산","구서명장#1 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 신양산-구서#1 T/L 안전이격확보용","2020-10-07 08:00","2020-10-08 18:00","2020-10-07 08:00","2020-10-08 18:00","연속"]
[691,"부산울산","동부산","신울산명례#1 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 신울산-명례#1 T/L 환경친화 도장공사 ○ 대상 : 26,27호","2020-10-22 08:00","2020-10-23 18:00","2020-10-22 08:00","2020-10-23 18:00","매일"]
[692,"부산울산","동부산","신울산명례#2 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 신울산-명례#2 T/L 환경친화 도장공사 ○ 대상 : 26,27호","2020-10-22 08:00","2020-10-23 18:00","2020-10-22 08:00","2020-10-23 18:00","매일"]
[693,"부산울산","동부산","명례고리NP T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 명례-고리 T/L 조류착지 방지장치 설치공사 ○ 대상 : 4개소","2020-10-27 08:00","2020-10-27 13:00","2020-10-27 08:00","2020-10-27 13:00","연속"]
[694,"부산울산","동부산","수영정보#2 T/L","수영S/S 154kV GIS 차단기 동작시험","1. 수영S/S 154kV GIS 차단기 동작시험(수영-정보#2T/L) 2. 정보S/S 154kV GIS 차단기 동작시험","2020-10-17 09:30","2020-10-17 17:00","2020-10-17 09:30","2020-10-17 17:00","연속"]
[695,"부산울산","동부산","정관고리NP T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 명례-고리 T/L 조류착지 방지장치 설치공사 ○ 대상 : 명례고리-4개소, 정관분기-19개소","2020-10-27 13:00","2020-10-29 18:00","2020-10-27 13:00","2020-10-29 18:00","연속"]
[696,"부산울산","동부산","명례정관 T/L","`20~21년도 동부산전력지사 가공송전 정비회사 총액공사","154kV 정관분기 T/L 조류착지 방지장치 설치공사 ○ 대상 : 정관분기-19개소","2020-10-28 08:00","2020-10-29 18:00","2020-10-28 08:00","2020-10-29 18:00","연속"]
[697,"부산울산","북부산","북부산구포#2 T/L","20-21 북부산전력지사 변전총액공사","구포S/S 154kV 북부산-구포#2T/L GIS하자점검 및 전자변교체","2020-10-26 10:00","2020-10-26 18:00","2020-10-26 10:00","2020-10-26 18:00","연속"]
[698,"부산울산","북부산","매리김해#1 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #1T/L 임시선로 구성(4회선, 호포-매리#1 포함) ○ 가철탑 24-1, 1-1호 설치","2020-10-31 07:00","2020-11-01 18:00","2020-10-31 07:00","2020-11-01 18:00","연속"]
[699,"부산울산","북부산","호포매리#1 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #1T/L 임시선로 구성(4회선, 매리-김해#1 포함) ○ 가철탑 24-1, 1-1호 설치","2020-10-31 07:00","2020-11-01 18:00","2020-10-31 07:00","2020-11-01 18:00","연속"]
[700,"부산울산","북부산","매리김해#2 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #2T/L 임시선로 구성(4회선, 호포-매리#2 포함) ○ 가철탑 24-1, 1-1호 설치","2020-10-24 07:00","2020-10-25 18:00","2020-10-24 07:00","2020-10-25 18:00","연속"]
[701,"부산울산","북부산","호포매리#2 T/L","154kV 호포-매리T/L 24호 변위철탑 교체공사","○ #2T/L 임시선로 구성(4회선, 매리-김해#2 포함) ○ 가철탑 24-1, 1-1호 설치","2020-10-24 07:00","2020-10-25 18:00","2020-10-24 07:00","2020-10-25 18:00","연속"]
[702,"부산울산","북부산","물금삼랑진PP#1 T/L","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사","154kV 물금-삼랑진#1T/L 피뢰기설치, 전선교체공사(33~58호, 36경간 7.994C-km)","2020-10-10 07:30","2020-11-04 18:00","2020-10-10 07:30","2020-11-04 18:00","연속"]
[703,"부산울산","북부산","물금삼랑진PP#2 T/L","20-21년 북부산전력지사 가공송전정비회사 총액공사","154kV 물금-삼랑진#2T/L 26~31호 소도체 이도조정","2020-10-05 08:00","2020-10-07 18:00","2020-10-05 08:00","2020-10-07 18:00","연속"]
[704,"부산울산","북부산","북부산물금 T/L","20-21년 북부산전력지사 가공송전정비회사 총액공사","154kV 북부산-물금T/L 13~17호 소도체 이도조정","2020-10-12 08:00","2020-10-14 18:00","2020-10-12 08:00","2020-10-14 18:00","연속"]
[705,"부산울산","북부산","언양산막#2 T/L","20-21 북부산전력지사 변전총액공사","산막S/S 154kV 언양-산막#2T/L GIS 전자변교체(H Type)","2020-10-23 10:00","2020-10-23 18:00","2020-10-23 10:00","2020-10-23 18:00","연속"]
[706,"부산울산","북부산","언양산막#1 T/L","20-21 북부산전력지사 변전총액공사","산막S/S 154kV 언양-산막#1T/L GIS 전자변교체(H Type)","2020-10-22 10:00","2020-10-22 18:00","2020-10-22 10:00","2020-10-22 18:00","연속"]
[707,"부산울산","북부산","삼계어방#1 T/L","2020년 북부산 가공송전 순시점검 위탁공사","154kV 삼계-어방T/L 정밀점검 ○구간 : 25~48호,C/H","2020-10-17 09:00","2020-10-18 18:00","2020-10-17 09:00","2020-10-18 18:00","매일"]
[708,"부산울산","북부산","삼계어방#2 T/L","2020년 북부산 가공송전 순시점검 위탁공사","154kV 삼계-어방T/L 정밀점검 ○구간 : 25~48호,C/H","2020-10-17 09:00","2020-10-18 18:00","2020-10-17 09:00","2020-10-18 18:00","매일"]
[709,"부산울산","북부산","한림정삼계#2 T/L","20-21 북부산전력지사 변전총액공사","삼계S/S 154kV 한림정-삼계#2T/L GIS 차단기 동작시험","2020-10-23 14:00","2020-10-23 18:00","2020-10-23 14:00","2020-10-23 18:00","연속"]
[710,"부산울산","북부산","한림정삼계#1 T/L","20-21 북부산전력지사 변전총액공사","삼계S/S 154kV 한림정-삼계#1T/L GIS 차단기 동작시험","2020-10-23 10:00","2020-10-23 14:00","2020-10-23 10:00","2020-10-23 14:00","연속"]
[711,"부산울산","북부산","엄궁학장#2 T/L","2020 북부산전력지사 154kV GIS 정밀점검","엄궁S/S 154kV 엄궁-학장#2T/L 정밀점검(DS 제외)","2020-10-29 09:00","2020-10-30 18:00","2020-10-29 09:00","2020-10-30 18:00","연속"]
[712,"부산울산","북부산","엄궁학장#1 T/L","2020 북부산전력지사 154kV GIS 정밀점검","엄궁S/S 154kV 엄궁-학장#1T/L 정밀점검(DS 제외)","2020-10-27 09:00","2020-10-28 18:00","2020-10-27 09:00","2020-10-28 18:00","연속"]
[713,"부산울산","북부산","북부산호포 T/L","20-21년 북부산전력지사 가공송전정비회사 총액공사","154kV 북부산-물금T/L 13~17호 소도체 이도조정을 위한 안전이격휴전선로","2020-10-12 08:00","2020-10-14 18:00","2020-10-12 08:00","2020-10-14 18:00","매일"]
[714,"부산울산","서부산","신김해지사#2 T/L","지사S/S 신김해-지사#2T/L GIS 차단기동작시험","지사S/S 신김해-지사#2T/L GIS 차단기동작시험","2020-10-12 10:00","2020-10-12 18:00","2020-10-12 10:00","2020-10-12 18:00","연속"]
[715,"부산울산","울산","동울산방어진 T/L","2020-21년 가공송전 정비회사 총액공사","ㅁ 피뢰기 설치 - 대상구간 : No.39,40","2020-10-12 07:00","2020-10-12 18:00","2020-10-12 07:00","2020-10-12 18:00","연속"]
[716,"부산울산","울산","신온산온산#2 T/L","송전선로 보호계전기 성능개선(세니온)","송전선로 보호계전기 성능개선(세니온)","2020-10-20 09:00","2020-10-20 18:00","2020-10-20 09:00","2020-10-20 18:00","연속"]
[717,"부산울산","울산","신온산온산#1 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- GIS 정밀점검 - 세니온 단거리 송전선로 보호반 성능개선 - 시험팀,보호제어과, 제작사 입회 필요 - 온산측 차단기 동작시험","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[718,"부산울산","울산","신울산S/S 154kV SEC B 67680","20-21년 변전정비회사 총액공사","- GIS 보통점검 및 전자변교체","2020-10-20 09:00","2020-10-20 18:00","2020-10-20 09:00","2020-10-20 18:00","연속"]
[719,"부산울산","울산","신울산S/S 154kV SEC B 62630","20-21년 변전정비회사 총액공사","- GIS 보통점검 및 전자변교체","2020-10-14 09:00","2020-10-14 18:00","2020-10-14 09:00","2020-10-14 18:00","연속"]
[720,"부산울산","울산","신울산S/S 154kV CB 6300","20-21년 변전정비회사 총액공사","- 6300 GCB 보통점검","2020-10-16 09:00","2020-10-16 18:00","2020-10-16 09:00","2020-10-16 18:00","연속"]
[721,"부산울산","울산","신울산S/S 154kV SEC B 65660","20-21년 변전정비회사 총액공사","- GIS 보통점검 및 전자변교체","2020-10-22 09:00","2020-10-22 18:00","2020-10-22 09:00","2020-10-22 18:00","연속"]
[722,"부산울산","울산","신울산웅촌#1 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- 웅촌측 GIS 정밀점검 - 신울산측 GIS 보통점검 및 전자변교체","2020-10-05 09:00","2020-10-06 18:00","2020-10-05 09:00","2020-10-06 18:00","연속"]
[723,"부산울산","울산","신울산S/S 154kV SEC CB 60610","20-21년 변전정비회사 총액공사","- GIS 보통점검 및 전자변교체","2020-10-21 09:00","2020-10-21 18:00","2020-10-21 09:00","2020-10-21 18:00","연속"]
[724,"부산울산","울산","신울산옥동#2 T/L","2019-2020년 북부산전력지사 지중송전 위탁정비공사","신울산구내 케이블헤드 및 피뢰기 점검","2020-10-15 13:00","2020-10-15 18:00","2020-10-15 13:00","2020-10-15 18:00","연속"]
[725,"부산울산","울산","신울산옥동#1 T/L","2019-2020년 북부산전력지사 지중송전 위탁정비공사","신울산구내 케이블헤드 및 피뢰기 점검","2020-10-15 09:00","2020-10-15 13:00","2020-10-15 09:00","2020-10-15 13:00","연속"]
[726,"부산울산","울산","신울산웅촌#2 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- 웅촌측 GIS 정밀점검 - 신울산측 GIS 보통점검 및 전자변교체","2020-10-07 09:00","2020-10-08 18:00","2020-10-07 09:00","2020-10-08 18:00","연속"]
[727,"부산울산","울산","신울산언양#2 T/L","2020년도 가공송전 순시점검 위탁공사","ㅁ 초기점검 - 대상철탑 : No. 64,65,66,66-1","2020-10-28 09:00","2020-10-29 18:00","2020-10-27 07:00","2020-10-27 18:00","연속"]
[728,"부산울산","울산","신울산언양#1 T/L","2020년도 가공송전 순시점검 위탁공사","ㅁ 초기점검 - 대상철탑 : No. 64,65,66,66-1","2020-10-26 09:00","2020-10-27 18:00","2020-10-26 09:00","2020-10-27 18:00","연속"]
[729,"부산울산","울산","두왕영남TP#1 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- #1Sh.C GIS 정밀점검 관련 시험가압1H","2020-10-22 17:00","2020-10-22 18:00","2020-10-22 17:00","2020-10-22 18:00","연속"]
[730,"부산울산","울산","옥동외동#1 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- #3M.Tr-1차 GIS 정밀점검 관련 시험가압1H","2020-10-20 17:00","2020-10-20 18:00","2020-10-20 17:00","2020-10-20 18:00","연속"]
[731,"부산울산","울산","옥동외동#2 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- 웅촌측 GIS 정밀점검","2020-10-14 09:00","2020-10-15 18:00","취소","취소","연속"]
[732,"부산울산","울산","옥동외동#1 T/L","2020-21년 가공송전 정비회사 총액공사","ㅁ 154kV 신울산-태화#2T/L 30호 부하측 내장애자 교체를 위한 휴전 - 특기사항 : 154kV 외동-옥동#1,2T/L 동시휴전 필요(병가철탑) - 작업장소 : 154kV 신울산-태화#2T/L No.30","2020-10-14 07:00","2020-10-14 10:00","취소","취소","연속"]
[733,"부산울산","울산","옥동외동#1 T/L","20년 하반기 울산전력지사 154kV 개폐장치 정밀점검 공사","- 웅촌측 GIS 정밀점검","2020-10-12 09:00","2020-10-13 18:00","2020-10-12 09:00","2020-10-13 18:00","연속"]
[734,"부산울산","울산","용연처용#2 T/L","345kV 남울산S/S 건설공사","계통변경 및 최초가압(154kV GIS)","2020-10-26 09:00","2020-10-28 18:00","2020-10-26 09:00","2020-10-28 18:00","연속"]
[735,"부산울산","울산","용연울산TP#1 T/L","20-21년 변전정비회사 총액공사","- GIS 하자점검 - LA 보통점검 - 최원재 과장님 PITR 정기시험 병행","2020-10-30 09:00","2020-10-30 18:00","2020-10-30 09:00","2020-10-30 18:00","연속"]
[736,"부산울산","울산","울산울산TP#1 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#2T/L GIS(627) #1DS, CB, 상부 철거 및 고깔 설치 후 시험가압선로(1H)","2020-10-30 17:00","2020-10-30 18:00","2020-10-30 17:00","2020-10-30 18:00","연속"]
[737,"부산울산","울산","울산울산TP#2 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 송전선 이설 : 구)울산-울산TP#2T/L -> 신)울산-울산TP#2T/L - 울산T/P 154kV (신)울산-울산TP#2T/L GIS(627) #65BUS 및 GIS 전체 시험가압 선로(24H이상)","2020-10-19 09:00","2020-10-22 18:00","2020-10-19 09:00","2020-10-22 18:00","연속"]
[738,"부산울산","울산","울산울산TP#1 T/L","345kV 신울산복합-북부산T/L 건설공사","345kV 신울산복합-북부산T/L 아킹혼 설치(154kV 병가철탑/안전이격)","2020-10-23 07:00","2020-10-23 18:00","2020-10-23 07:00","2020-10-23 18:00","연속"]
[739,"부산울산","울산","울산T/P 154kV #60 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#1T/L GIS(617) #1DS, CB, 부싱, GIB 철거 - 울산T/P 154kV (신)울산-울산TP#2T/L GIS(627) #1DS, CB, 부싱, GIB 설치","2020-10-08 09:00","2020-10-15 18:00","2020-10-08 09:00","2020-10-15 18:00","연속"]
[740,"부산울산","울산","울산울산TP#2 T/L","345kV 신울산복합-북부산T/L 건설공사","345kV 신울산복합-북부산T/L 아킹혼 설치(154kV 병가철탑/안전이격)","2020-10-24 07:00","2020-10-24 18:00","2020-10-24 07:00","2020-10-24 18:00","연속"]
[741,"부산울산","울산","울산T/P 154kV #60 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#2T/L GIS(627) #1DS, CB, 상부 철거 및 고깔 설치","2020-10-27 09:00","2020-10-30 18:00","2020-10-27 09:00","2020-10-30 18:00","연속"]
[742,"부산울산","울산","울산울산TP#1 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#2T/L GIS(627) #2DS철거 및 고깔 설치 후 #65BUS 시험가압 선로(1H)","2020-10-26 17:00","2020-10-26 18:00","2020-10-26 17:00","2020-10-26 18:00","연속"]
[743,"부산울산","울산","울산T/P 154kV #65 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#2T/L GIS(627) #2DS 철거 및 고깔설치","2020-10-26 09:00","2020-10-26 18:00","2020-10-26 09:00","2020-10-26 18:00","연속"]
[744,"부산울산","울산","울산울산TP#1 T/L","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#1T/L GIS(617) #2DS철거 및 고깔 설치 후 #65BUS 시험가압 선로(1H)","2020-10-07 17:00","2020-10-07 18:00","2020-10-07 17:00","2020-10-07 18:00","연속"]
[745,"부산울산","울산","울산T/P 154kV #65 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#1T/L GIS(617) #2DS 철거 및 고깔설치","2020-10-07 09:00","2020-10-07 18:00","2020-10-07 09:00","2020-10-07 18:00","연속"]
[746,"부산울산","울산","울산T/P 154kV #60 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (신)울산-울산TP#2T/L GIS(627) #1DS(#60BUS) 시험가압","2020-10-22 17:00","2020-10-22 18:00","2020-10-22 17:00","2020-10-22 18:00","연속"]
[747,"부산울산","울산","용연울산TP#3 T/L","345kV 신울산복합-북부산T/L 건설공사","345kV 신울산복합-북부산T/L 아킹혼 설치(154kV 병가철탑/안전이격)","2020-10-17 07:00","2020-10-17 18:00","2020-10-17 07:00","2020-10-17 18:00","연속"]
[748,"부산울산","울산","울산T/P 154kV #65 BUS","2020년 울산화력S/Y 154kV 장기사용 GIS 교체공사","- 울산T/P 154kV (구)울산-울산TP#1T/L GIS(617) #2DS GIB 철거 - 울산T/P 154kV (신)울산-울산TP#2T/L GIS(627) #2DS, GIB 설치","2020-10-16 09:00","2020-10-22 17:00","2020-10-16 09:00","2020-10-22 17:00","연속"]