{"text_format":"2","workbook":"xls","n_sheets":11,"sheets":["공통","Analog Input List","Digital Input List","Analog Output List","선로","변압기","차단기 및 단로기","모선","SHR","SC","발전기"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"공통","index":0,"n_rows":3,"n_cols":2,"rows_kept":3,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["기본 자료"]
[null,"- 단선결선도(기기번호부여된 것)"]
[null,"- RTU 포인트 List"]

{"sheet":"Analog Input List","index":1,"n_rows":34,"n_cols":7,"rows_kept":34,"cut":false,"hidden":false,"merged":[[0,3,0,6],[1,3,1,4],[1,5,1,6],[0,0,2,0],[0,1,2,1],[0,2,2,2]],"flags":["formulas_cached_only"]}
["DNP Index","설비명","Analog","TD Scale"]
[null,null,null,"최소",null,"최대"]
[null,null,null,"mA ","지시값","mA","지사값"]
[0,"예) 송전선로#1","MW",0,0,1,3600]
[1,"예) 송전선로#1","MVAR",0,0,1,3600]
[2,"예) 345kV #1 모선","kV ",0,0,1,450]
[3,"예) #1 변압기 2차","MW",0,0,1,860]
[4,"예) #1 변압기 2차","MVAR",0,0,1,860]
[5,"예) #1 변압기 2차","Tap",0,0,1,17]
[6,"예) Shr #1","MVAR",0,0,1,860]
[7,"예) SC #1","MVAR",0,0,1,860]
[8,"예) #1 발전기 송전단","MW",4,-500,20,500]
[9,"예) #1 발전기 송전단","MVAR",4,-500,20,500]
[10,"예) #1 발전기 발전단","MW",4,-500,20,500]
[11,"예) #1 발전기 발전단","MVAR",4,-500,20,500]
[12,"예) #1 발전기 AGC High Limit","HMW",4,0,20,500]
[13,"예) #1 발전기 AGC Low Limit","LMW",4,0,20,500]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]

{"sheet":"Digital Input List","index":2,"n_rows":33,"n_cols":5,"rows_kept":33,"cut":false,"hidden":false,"merged":[[0,3,0,4],[0,0,1,0],[0,1,1,1],[0,2,1,2]],"flags":["formulas_cached_only"]}
["DNP Index","설비명","Point","접점"]
[null,null,null,"A접점","B접점"]
[0,"예) 차단기 #1","CB"]
[1,"예) 단로기 #1","DS"]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]

{"sheet":"Analog Output List","index":3,"n_rows":13,"n_cols":5,"rows_kept":13,"cut":false,"hidden":false,"merged":[[0,3,0,4],[0,0,1,0],[0,1,1,1],[0,2,1,2]],"flags":["formulas_cached_only"]}
["DNP Index","설비명","Analog","Scale"]
[null,null,null,"최소","최대"]
[0,"예)#1 발전기 AGC Target","MW",0,500]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]

{"sheet":"선로","index":4,"n_rows":12,"n_cols":10,"rows_kept":12,"cut":false,"hidden":false,"merged":[[3,1,3,2],[2,1,2,2],[1,1,1,2],[1,3,1,8],[2,3,2,8],[3,3,3,8],[4,1,5,1],[6,3,6,5],[7,3,7,5],[6,1,11,1],[9,3,9,5],[6,2,8,2],[9,2,11,2],[11,3,11,5],[8,3,8,5],[6,6,6,8],[10,3,10,5],[10,6,10,8],[11,6,11,8],[7,6,7,8],[8,6,8,8],[9,6,9,8]],"flags":["formulas_cached_only"]}
["송전선로 자료"]
[null,"명      칭",{"$nulls":7},"선로명칭 및 구간표시(00SS~xxSS)"]
[null,"전      압",{"$nulls":7},"공칭전압으로 표시(예:154kV,345kV,765kV)"]
[null,"허용전류(허용용량)",{"$nulls":7},"A(MVA)로 표시"]
[null,"임피던스","정상","R",null,"X",null,"Y",null,"%Z로 표시(R:저항성분,X:인덕턴스성분,Y:어드미턴스성분)"]
[null,null,"영상","R",null,"X",null,"Y",null,"%Z로 표시(R:저항성분,X:인덕턴스성분,Y:어드미턴스성분)"]
[null,"RTU AI ","MW","Address",{"$nulls":5},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MW값 ~ 1mA 에서 MW값\n- 4mA~20mA -> 4mA에서 MW값 ~ 20mA 에서 MW값"]
[null,null,"MVAR","Address",{"$nulls":5},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]

{"sheet":"변압기","index":5,"n_rows":25,"n_cols":11,"rows_kept":25,"cut":false,"hidden":false,"merged":[[16,1,24,1],[22,2,24,3],[22,4,22,6],[22,7,22,9],[23,4,23,6],[23,7,23,9],[24,4,24,6],[24,7,24,9],[19,2,21,3],[20,7,20,9],[11,2,14,2],[15,2,15,3],[10,1,15,1],[15,4,15,9],[10,4,10,9],[11,4,11,9],[10,2,10,3],[12,4,12,9],[13,4,13,9],[5,2,5,3],[6,1,6,3],[8,2,8,3],[9,2,9,3],[7,2,7,3],[18,7,18,9],[16,2,18,3],[7,1,9,1],[7,4,7,9],[6,4,6,9],[1,4,1,9],[3,4,3,9],[1,1,1,3],[2,1,2,3],[3,2,3,3],[4,2,4,3],[2,4,2,9],[3,1,5,1],[4,4,4,9],[5,4,5,9],[16,4,16,6],[16,7,16,9],[17,4,17,6],[17,7,17,9],[18,4,18,6],[21,4,21,6],[21,7,21,9],[19,4,19,6],[19,7,19,9],[20,4,20,6]],"flags":["formulas_cached_only"]}
["변압기 자료"]
[null,"명      칭"]
[null,"권  선  수",{"$nulls":8},"2권선,3권선"]
[null,"전압","1차",{"$nulls":7},"변압기 1차 정격전압"]
[null,null,"2차",{"$nulls":7},"변압기 2차 정격전압"]
[null,null,"3차",{"$nulls":7},"변압기 3차 정격전압(3권선인 경우)"]
[null,"정격용량",{"$nulls":8},"MVA로 표시"]
[null,"임피던스","기준용량",{"$nulls":7},"임피던스 계산에 적용된 기준용량"]
[null,null,"정상",null,"1~2차",null,"1~3차",null,"2~3차",null,"%Z로 표시(인덕턴스성분)"]
[null,null,"영상",null,"1~2차",null,"1~3차",null,"2~3차",null,"%Z로 표시(인덕턴스성분)"]
[null,"Tap","Type",{"$nulls":7},"NLTC,ULTC"]
[null,null,"변경\n범위","Max",{"$nulls":6},"Max Tap"]
[null,null,null,"Min",{"$nulls":6},"Min Tap"]
[null,null,null,"Nominal",{"$nulls":6},"정격 전압 Tap"]
[null,null,null,"Step",{"$nulls":6},"Tap간 %z"]
[null,null,"Normal",{"$nulls":7},"정상 운전 Tap"]
[null,"RTU AI ","MW",null,"Address",{"$nulls":5},"AI 할당 포인트"]
[{"$nulls":4},"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[{"$nulls":4},"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MW값 ~ 1mA 에서 MW값\n- 4mA~20mA -> 4mA에서 MW값 ~ 20mA 에서 MW값"]
[null,null,"MVAR",null,"Address",{"$nulls":5},"AI 할당 포인트"]
[{"$nulls":4},"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[{"$nulls":4},"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"Tap 위치",null,"Address",{"$nulls":5},"AI 할당 포인트"]
[{"$nulls":4},"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[{"$nulls":4},"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]

{"sheet":"차단기 및 단로기","index":6,"n_rows":8,"n_cols":10,"rows_kept":8,"cut":false,"hidden":false,"merged":[[6,1,7,2],[5,1,5,2],[5,3,5,8],[4,1,4,2],[4,3,4,8],[6,3,6,5],[6,6,6,8],[7,3,7,5],[7,6,7,8],[1,1,1,2],[1,3,1,8],[3,1,3,2],[3,3,3,8],[2,1,2,2],[2,3,2,8]],"flags":["formulas_cached_only"]}
["차단기 및 단로기"]
[null,"명      칭",{"$nulls":7},"차단기 및 단로기 번호"]
[null,"Type",{"$nulls":7},"차단기 or 단로기"]
[null,"전      압",{"$nulls":7},"공칭전압으로 표시(예:154kV,345kV,765kV)"]
[null,"차단용량",{"$nulls":7},"A로 표시"]
[null,"Normal Status",{"$nulls":7},"정상 운전시 운전상태"]
[null,"RTU DI ",null,"Address",{"$nulls":5},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":5},"A, B접점"]

{"sheet":"모선","index":7,"n_rows":6,"n_cols":11,"rows_kept":6,"cut":false,"hidden":false,"merged":[[5,7,5,9],[3,2,5,3],[2,4,2,9],[2,1,2,3],[1,1,1,3],[1,4,1,9],[3,1,5,1],[3,4,3,6],[3,7,3,9],[4,4,4,6],[4,7,4,9],[5,4,5,6]],"flags":["formulas_cached_only"]}
["모선 자료"]
[null,"명      칭"]
[null,"전압",{"$nulls":8},"정격 전압"]
[null,"RTU AI ","kV",null,"Address",{"$nulls":5},"AI 할당 포인트"]
[{"$nulls":4},"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[{"$nulls":4},"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 kVr값 ~ 1mA 에서 kV값\n- 4mA~20mA -> 4mA에서 kV값 ~ 20mA 에서 kVr값"]

{"sheet":"SHR","index":8,"n_rows":7,"n_cols":10,"rows_kept":7,"cut":false,"hidden":false,"merged":[[4,6,4,8],[5,3,5,5],[5,6,5,8],[6,3,6,5],[1,1,1,2],[1,3,1,8],[2,1,2,2],[2,3,2,8],[4,1,6,1],[6,6,6,8],[3,1,3,2],[3,3,3,8],[4,2,6,2],[4,3,4,5]],"flags":["formulas_cached_only"]}
["S.Hr 자료"]
[null,"명      칭"]
[null,"전      압",{"$nulls":7},"공칭전압으로 표시(예:154kV,345kV,765kV)"]
[null,"용      량",{"$nulls":7},"MVAR로 표시"]
[null,"RTU AI ","MVAR","Address",{"$nulls":5},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]

{"sheet":"SC","index":9,"n_rows":7,"n_cols":10,"rows_kept":7,"cut":false,"hidden":false,"merged":[[4,1,6,1],[4,2,6,2],[4,3,4,5],[4,6,4,8],[5,3,5,5],[5,6,5,8],[6,3,6,5],[6,6,6,8],[1,1,1,2],[1,3,1,8],[2,1,2,2],[2,3,2,8],[3,1,3,2],[3,3,3,8]],"flags":["formulas_cached_only"]}
["SC 자료"]
[null,"명      칭"]
[null,"전      압",{"$nulls":7},"공칭전압으로 표시(예:154kV,345kV,765kV)"]
[null,"용      량",{"$nulls":7},"MVAR로 표시"]
[null,"RTU AI ","MVAR","Address",{"$nulls":5},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":5},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":5},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]

{"sheet":"발전기","index":10,"n_rows":64,"n_cols":13,"rows_kept":64,"cut":false,"hidden":false,"merged":[[33,4,33,11],[28,2,30,2],[54,1,63,1],[55,4,55,11],[56,4,56,11],[54,2,55,2],[56,2,57,2],[57,4,57,11],[54,4,54,11],[52,1,53,1],[20,4,20,11],[62,2,63,2],[62,4,62,11],[63,4,63,11],[49,2,51,2],[49,4,49,11],[50,4,50,11],[51,4,51,11],[31,2,33,2],[31,4,31,11],[16,4,16,11],[17,4,17,11],[18,2,18,3],[19,2,19,3],[18,1,19,1],[20,1,21,1],[20,2,20,3],[21,2,21,3],[16,2,16,3],[17,2,17,3],[60,2,61,2],[60,4,60,11],[61,4,61,11],[58,2,59,2],[58,4,58,11],[59,4,59,11],[46,2,48,2],[46,4,46,11],[47,4,47,11],[48,4,48,11],[52,2,53,2],[52,4,52,11],[53,4,53,11],[41,4,41,11],[42,4,42,11],[40,2,42,2],[43,2,45,2],[43,4,43,11],[44,4,44,11],[45,4,45,11],[37,2,39,2],[37,4,37,11],[38,4,38,11],[39,4,39,11],[22,1,24,1],[23,4,23,11],[24,4,24,11],[25,4,25,11],[22,2,24,2],[25,2,27,2],[26,4,26,11],[27,4,27,11],[25,1,51,1],[32,4,32,11],[40,4,40,11],[12,4,12,11],[13,4,13,11],[14,4,14,11],[22,4,22,11],[21,4,21,11],[15,4,15,11],[28,4,28,11],[29,4,29,11],[30,4,30,11],[12,1,14,1],[12,2,12,3],[13,2,13,3],[14,2,14,3],[15,1,17,1],[15,2,15,3],[1,4,1,11],[2,4,2,11],[6,4,6,11],[7,4,7,11],[3,4,3,11],[4,4,4,11],[5,4,5,11],[8,12,9,12],[8,2,8,3],[9,2,9,3],[8,4,8,11],[9,4,9,11],[10,1,11,1],[10,2,10,3],[11,2,11,3],[10,4,10,11],[11,4,11,11],[34,2,36,2],[34,4,34,11],[35,4,35,11],[36,4,36,11],[1,1,1,3],[6,1,6,3],[2,1,2,3],[7,1,7,3],[3,1,5,2],[8,1,9,1]],"flags":["formulas_cached_only"]}
["발전기 자료"]
[null,"명      칭"]
[null,"Type",{"$nulls":10},"NP,TP,HP,PP,GT,ST"]
[null,"연료 종류",null,"종류",{"$nulls":8},"원자력,수력,역청탄,국내탄,중유,경유.LNG,소각로,등…"]
[null,null,null,"발열량",{"$nulls":8},"Kcal/kg"]
[null,null,null,"열량단가",{"$nulls":8},"천원/Gcal"]
[null,"단자 전압",{"$nulls":10},"Kv로 표시"]
[null,"정격용량",{"$nulls":10},"MVA로 표시"]
[null,"무효전력 \n제한치","Max",{"$nulls":9},"MW Var로 표시\nMW 출력에 대한 MVAR 출력 Garph로 제공해야 함 "]
[null,null,"Min"]
[null,"Dynamic model \nparameter","Mechanical Inertia",{"$nulls":9},"pu MW· Sec/MVA"]
[null,null,"Damping coefficient",{"$nulls":9},"pu MW/pu Hz"]
[null,"임피던스","과도 리엑턴스",{"$nulls":9},"%z(100MVA Base)"]
[null,null,"차과도 리엑턴스",{"$nulls":9},"%z(100MVA Base)"]
[null,null,"영상 리엑턴스",{"$nulls":9},"%z(100MVA Base)"]
[null,"(1차연료) 입출력 특성계수","2차 계수"]
[null,null,"1차 계수"]
[null,null,"상수항"]
[null,"소내소비계수","1차 계수"]
[null,null,"상수항"]
[null,"증,감발률","증발률",{"$nulls":9},"MW/mim"]
[null,null,"감발률",{"$nulls":9},"MW/mim"]
[null,"RTU AI ","발전단 MW\n(발전기 단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MW값 ~ 1mA 에서 MW값\n- 4mA~20mA -> 4mA에서 MW값 ~ 20mA 에서 MW값"]
[null,"RTU AI ","발전단 MVAR\n(발전기 단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"송전단 MW\n(발전기 단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MW값 ~ 1mA 에서 MW값\n- 4mA~20mA -> 4mA에서 MW값 ~ 20mA 에서 MW값"]
[null,null,"송전단 MVAR\n(발전기 단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"kV\n(발전기 단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"HMW\n(AGC High Limit MW)\n(발전기 단위,ST제외)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"LMW\n(AGC Low Limit MW)\n(발전기 단위,ST제외)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"RL\n(분당 증감발율)\n(발전기 단위,ST 제외)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"Target\n(Feedback AGC Set Point)\n(AGC 제어단위)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,null,"AUX MW\n(보조 변압기 부하)","Address",{"$nulls":8},"AI 할당 포인트"]
[null,null,null,"TD사양",{"$nulls":8},"0mA~1mA, 4~20mA"]
[null,null,null,"Range",{"$nulls":8},"- 0mA~1mA -> 0mA에서 MVar값 ~ 1mA 에서 MVar값\n- 4mA~20mA -> 4mA에서 MVar값 ~ 20mA 에서 MVar값"]
[null,"RTU AO ","Target\n(AGC 제어단위)","Address",{"$nulls":8},"AO 할당 포인트"]
[null,null,null,"Range",{"$nulls":8},"MW 범위"]
[null,"RTU DI ","AMU\n(AGC 운전 모드)\n(발전기 단위,ST 제외)","Address",{"$nulls":8},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":8},"A, B접점"]
[null,null,"HMW\n(AGC High Limit 접점)\n(발전기 단위,ST 제외)","Address",{"$nulls":8},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":8},"A, B접점"]
[null,null,"LMW\n(AGC Low Limit 접점)\n(발전기 단위,ST제외)","Address",{"$nulls":8},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":8},"A, B접점"]
[null,null,"MOD\n(복합 운전 모드,양수 모드)\n(발전기 단위,ST 제외 )","Address",{"$nulls":8},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":8},"A, B접점"]
[null,null,"GF\n(Governor Free 접점)\n(발전기 단위, ST 제외)","Address",{"$nulls":8},"DI 할당 포인트"]
[null,null,null,"접점",{"$nulls":8},"A, B접점"]